## 14.1-IO Database
PMT: | [5 empty] | Design Institute: |  |  | Project No. | P-OKITM07-10 | [6 empty] | EXCHANGE COMMUNICTION LIST
[9 empty] | Project Name | DETAIL ENGINEERING FOR 4(FOUR) UNITS TISSUE MACHINE
[9 empty] | Doc. No. | P-OKITM07-10-320-06-LST-3005 | [7 empty] | Abbreviations
Owner: | [8 empty] | Rev. No. | 4 |  |  | Prep'd by | Dengzuijie |  |  |  | EER Electronic Equipment Room |  |  |  | SQRT Square Root
[9 empty] | Purpose | Final |  |  | Chk'd by | Chengjianguo |  |  |  | CCR Control Center Room
[9 empty] | Date | 8,30,2021 |  |  | Appv'd by | LiXiangdong |  |  |  | ESP Electrostatic Precipitator
P&ID No. | Area | JB No. | ASD No. | Loop No. | Tag No. | System Tag No. | Service Description | Signal Tag | Instrument Type | Location | System | IO Type | Signal |  |  | IO Loc. | PV LO | PV HI | Eng. Unit | Alarm | [6 empty] | State "0" | State "1" | CV Fail Action | CV Ctrl Action | PV CHAR | From |  | Cable |  |  | To |  | Rev. | Supply | Remarks
[13 empty] | Type | Power | Wire |  |  |  |  | LLL | LL | L | Nor. | H | HH | HHH | [5 empty] | JB/Panel No. | TB | Cable Number | Cable Type | Cable Order | Cabinet No. | TB |  | By
MACHINE BROKE
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD102 |  | TM140117FS001 | TM140117FS001 | TM140117FS001.L | SEALING WATER TO YANKEE PULPER PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD111 |  | TM140117FS002 | TM140117FS002 | TM140117FS002.L | SEALING WATER TO BROKE DEFLAKED CHEST PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD112 |  | TM140117FS003 | TM140117FS003 | TM140117FS003.L | SEALING WATER TO BROKE INTERIM TOWER PUMP 2 FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS005 | TM140117SV005 | TM140117SV005 | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS103 |  | TM140117HS005 | TM140117SV005.ZSC | TM140117SV005.GSC | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS103 |  | TM140117HS005 | TM140117SV005.ZSO | TM140117SV005.GSO | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS103 |  | TM140117HS005 | TM140117EV005 | TM140117EV005 | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS006 | TM140117SV006 | TM140117SV006 | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS103 |  | TM140117HS006 | TM140117SV006.ZSC | TM140117SV006.GSC | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS103 |  | TM140117HS006 | TM140117SV006.ZSO | TM140117SV006.GSO | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS103 |  | TM140117HS006 | TM140117EV006 | TM140117EV006 | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA103 |  | TM140117LC007 | TM140117LT007 | TM140117LT007.MV | YANKEE PULPER LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 5000 | mm |  | 20% | 30% |  | 80% | 90% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA103 | TM1401ASD104 | TM140117LC007 | TM140117LV007A | TM140117LV007A.OUT | YANKEE PULPER LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA103 | TM1401ASD104 | TM140117LC007 | TM140117LV007B | TM140117LV007B.OUT | YANKEE PULPER LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA103 | TM1401ASD104 | TM140117LC007 | TM140117LV007C | TM140117LV007C.OUT | YANKEE PULPER LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117EC008 | TM140117EX008 | TM140117EX008.SOF | YANKEE PULPER SHEET BREAK | EX | DCS software function | DCS | DCS |  | Software function | [25 empty] | B
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD102 |  | TM140117FS009 | TM140117FS009 | TM140117FS009.L | SEALING WATER TO YANKEE PULPER RECIRCULATION PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD102 |  | TM140117FS010 | TM140117FS010 | TM140117FS010.L | SEALING WATER TO YANKEE PULPER AGITATOR FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS011 | TM140117SV011 | TM140117SV011 | YANKEE PULPER SHOWER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS103 |  | TM140117HS011 | TM140117SV011.ZSC | TM140117SV011.GSC | YANKEE PULPER SHOWER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS103 |  | TM140117HS011 | TM140117SV011.ZSO | TM140117SV011.GSO | YANKEE PULPER SHOWER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS103 |  | TM140117HS011 | TM140117EV011 | TM140117EV011 | YANKEE PULPER SHOWER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117NC012 | TM140117NE012 |  | PULP FROM YANKEE PULPER TO BROKE INTERIM TOWER CONSISTENCY | NE | Blade Consistency Sensor | Field | [28 empty] | 0
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA103 |  | TM140117NC012 | TM140117NT012 | TM140117NT012.MV | PULP FROM YANKEE PULPER TO BROKE INTERIM TOWER CONSISTENCY | NT | Blade Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 6 | %Cs | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117FC113 | TM140117FE113 |  | DILUTITION WATER TO YANKEE PULPER FLOW | FE | Magnetic Flow Sensor | Field | DCS | [27 empty] | B
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA103 |  | TM140117FC113 | TM140117FT113 | TM140117FT113.MV | DILUTITION WATER TO YANKEE PULPER FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 3500 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA103 | TM1401ASD104 | TM140117FC113 | TM140117FV113 | TM140117FV113.OUT | DILUTITION WATER TO YANKEE PULPER FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1402JBA112 |  | TM140117LI015 | TM140117LT015 | TM140117LT015.MV | BROKE INTERIM TOWER LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 12600 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS016 | TM140117SV016 | TM140117SV016 | PULP FROM BROKE INTERIM TOWER TO BROKE INTERIM TOWER PUMP 2 ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1402JBS113 |  | TM140117HS016 | TM140117SV016.ZSC | TM140117SV016.GSC | PULP FROM BROKE INTERIM TOWER TO BROKE INTERIM TOWER PUMP 2 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1402JBS113 |  | TM140117HS016 | TM140117SV016.ZSO | TM140117SV016.GSO | PULP FROM BROKE INTERIM TOWER TO BROKE INTERIM TOWER PUMP 2 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1402JBS113 |  | TM140117HS016 | TM140117EV016 | TM140117EV016 | PULP FROM BROKE INTERIM TOWER TO BROKE INTERIM TOWER PUMP 2 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1402JBA112 | TM1402ASD113 | TM140117HC017 | TM140117HV017 | TM140117HV017.OUT | BROKE INTERIM TOWER PUMP 1 INLET DILUTION WATER CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS020 | TM140117SV020 | TM140117SV020 | PULP FROM BROKE INTERIM TOWER TO PUMP 1 ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1402JBS113 |  | TM140117HS020 | TM140117SV020.ZSC | TM140117SV020.GSC | PULP FROM BROKE INTERIM TOWER TO PUMP 1 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1402JBS113 |  | TM140117HS020 | TM140117SV020.ZSO | TM140117SV020.GSO | PULP FROM BROKE INTERIM TOWER TO PUMP 1 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1402JBS113 |  | TM140117HS020 | TM140117EV020 | TM140117EV020 | PULP FROM BROKE INTERIM TOWER TO PUMP 1 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS021 | TM140117SV021 | TM140117SV021 | HC-CLEANER FEED ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS201 |  | TM140117HS021 | TM140117SV021.ZSC | TM140117SV021.GSC | HC-CLEANER FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS201 |  | TM140117HS021 | TM140117SV021.ZSO | TM140117SV021.GSO | HC-CLEANER FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS201 |  | TM140117HS021 | TM140117EV021 | TM140117EV021 | HC-CLEANER FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS022 | TM140117SV022 | TM140117SV022 | HC-CLEANER ACCEPT ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS201 |  | TM140117HS022 | TM140117SV022.ZSC | TM140117SV022.GSC | HC-CLEANER ACCEPT ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS201 |  | TM140117HS022 | TM140117SV022.ZSO | TM140117SV022.GSO | HC-CLEANER ACCEPT ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS201 |  | TM140117HS022 | TM140117EV022 | TM140117EV022 | HC-CLEANER ACCEPT ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS023 | TM140117SV023 | TM140117SV023 | HC-CLEANER BYPASS ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS201 |  | TM140117HS023 | TM140117SV023.ZSC | TM140117SV023.GSC | HC-CLEANER BYPASS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS201 |  | TM140117HS023 | TM140117SV023.ZSO | TM140117SV023.GSO | HC-CLEANER BYPASS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS201 |  | TM140117HS023 | TM140117EV023 | TM140117EV023 | HC-CLEANER BYPASS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA201 |  | TM140117PC028 | TM140117PT028 | TM140117PT028.MV | HC-CLEANER FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA201 |  | TM140117PC029 | TM140117PT029 | TM140117PT029.MV | HC-CLEANER ACCEPT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA201 | TM1401ASD201 | TM140117PC029 | TM140117PV029 | TM140117PV029.OUT | HC-CLEANER ACCEPT PRESSURE CV SETPOINT | PV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117KS031 | TM140117KX031 | TM140117KX031.SOF | HC-CLEANER JUNK TRAP SEQUENCE | KX | DCS software function | DCS | DCS |  | Software function
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS031A | TM140117SV031A | TM140117SV031A | HC-CLEANER REJECT TOP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD203 |  | TM140117HS031A | TM140117SV031A.ZSC | TM140117SV031A.GSC | HC-CLEANER REJECT TOP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD203 |  | TM140117HS031A | TM140117SV031A.ZSO | TM140117SV031A.GSO | HC-CLEANER REJECT TOP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD203 | TM1401ASD202 | TM140117HS031A | TM140117EV031A | TM140117EV031A | HC-CLEANER REJECT TOP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS031B | TM140117SV031B | TM140117SV031B | HC-CLEANER REJECT BOTTOM ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD203 |  | TM140117HS031B | TM140117SV031B.ZSC | TM140117SV031B.GSC | HC-CLEANER REJECT BOTTOM ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD203 |  | TM140117HS031B | TM140117SV031B.ZSO | TM140117SV031B.GSO | HC-CLEANER REJECT BOTTOM ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD203 | TM1401ASD202 | TM140117HS031B | TM140117EV031B | TM140117EV031B | HC-CLEANER REJECT BOTTOM ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS031C | TM140117SV031C | TM140117SV031C | HC-CLEANER REJECT TOP FLUSHING ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD203 |  | TM140117HS031C | TM140117SV031C.ZSC | TM140117SV031C.GSC | HC-CLEANER REJECT TOP FLUSHING ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD203 |  | TM140117HS031C | TM140117SV031C.ZSO | TM140117SV031C.GSO | HC-CLEANER REJECT TOP FLUSHING ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD203 | TM1401ASD202 | TM140117HS031C | TM140117EV031C | TM140117EV031C | HC-CLEANER REJECT TOP FLUSHING ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS031D | TM140117SV031D | TM140117SV031D | HC-CLEANER REJECT BOTTOM FLUSHING ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD203 |  | TM140117HS031D | TM140117SV031D.ZSC | TM140117SV031D.GSC | HC-CLEANER REJECT BOTTOM FLUSHING ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD203 |  | TM140117HS031D | TM140117SV031D.ZSO | TM140117SV031D.GSO | HC-CLEANER REJECT BOTTOM FLUSHING ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD203 | TM1401ASD202 | TM140117HS031D | TM140117EV031D | TM140117EV031D | HC-CLEANER REJECT BOTTOM FLUSHING ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS031E | TM140117SV031E | TM140117SV031E | HC-CLEANER REJECT EXHAUSTING ON/OFF VALVE OPENED | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD203 |  | TM140117HS031E | TM140117SV031E.ZSC | TM140117SV031E.GSC | HC-CLEANER REJECT EXHAUSTING ON/OFF VALVE OPENED CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD203 |  | TM140117HS031E | TM140117SV031E.ZSO | TM140117SV031E.GSO | HC-CLEANER REJECT EXHAUSTING ON/OFF VALVE OPENED OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD203 | TM1401ASD202 | TM140117HS031E | TM140117EV031E | TM140117EV031E | HC-CLEANER REJECT EXHAUSTING ON/OFF VALVE OPENED SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA101 |  | TM140117LC032 | TM140117LT032 | TM140117LT032.MV | THICKENER BROKE TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS034 | TM140117SV034 | TM140117SV034 | BROKE DEFLAKER FLUSHING ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS203 |  | TM140117HS034 | TM140117SV034.ZSC | TM140117SV034.GSC | BROKE DEFLAKER FLUSHING ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS203 |  | TM140117HS034 | TM140117SV034.ZSO | TM140117SV034.GSO | BROKE DEFLAKER FLUSHING ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS203 |  | TM140117HS034 | TM140117EV034 | TM140117EV034 | BROKE DEFLAKER FLUSHING ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS035 | TM140117SV035 | TM140117SV035 | BROKE DEFLAKER FEED ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS203 |  | TM140117HS035 | TM140117SV035.ZSC | TM140117SV035.GSC | BROKE DEFLAKER FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS203 |  | TM140117HS035 | TM140117SV035.ZSO | TM140117SV035.GSO | BROKE DEFLAKER FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS203 |  | TM140117HS035 | TM140117EV035 | TM140117EV035 | BROKE DEFLAKER FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS036 | TM140117SV036 | TM140117SV036 | BROKE DEFLAKER ACCEPT ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS203 |  | TM140117HS036 | TM140117SV036.ZSC | TM140117SV036.GSC | BROKE DEFLAKER ACCEPT ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS203 |  | TM140117HS036 | TM140117SV036.ZSO | TM140117SV036.GSO | BROKE DEFLAKER ACCEPT ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS203 |  | TM140117HS036 | TM140117EV036 | TM140117EV036 | BROKE DEFLAKER ACCEPT ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS037 | TM140117SV037 | TM140117SV037 | BROKE DEFLAKER BYPASS ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS203 |  | TM140117HS037 | TM140117SV037.ZSC | TM140117SV037.GSC | BROKE DEFLAKER BYPASS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS203 |  | TM140117HS037 | TM140117SV037.ZSO | TM140117SV037.GSO | BROKE DEFLAKER BYPASS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS203 |  | TM140117HS037 | TM140117EV037 | TM140117EV037 | BROKE DEFLAKER BYPASS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA201 |  | TM140117PI038 | TM140117PT038 | TM140117PT038.MV | BROKE DEFLAKER FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117FC039 | TM140117FE039 |  | STOCK TO BROKE DEFLAKED CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA101 |  | TM140117FC039 | TM140117FT039 | TM140117FT039.MV | STOCK TO BROKE DEFLAKED CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 720 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA101 | TM1401ASD101 | TM140117FC039 | TM140117FV039 | TM140117FV039.OUT | STOCK TO BROKE DEFLAKED CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117WC040 | TM140117WX040 | TM140117WX040.SOF | BROKE DEFLAKER SEC SETPOINT | WX | DCS software function | DCS | DCS |  | Software function
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD201 |  | TM140117FS041 | TM140117FS041 | TM140117FS041.L | SEALING WATER TO BROKE DEFLAKER FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA112 |  | TM140117LC042 | TM140117LT042 | TM140117LT042.MV | BROKE DEFLAKED CHEST LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA112 | TM1401ASD112 | TM140117LC042 | TM140117LV042 | TM140117LV042.OUT | BROKE DEFLAKED CHEST LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117NC044 | TM140117NE044 |  | DEFLAKED BROKE TO MIXING CHEST CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230 VAC | [24 empty] | B
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA112 |  | TM140117NC044 | TM140117NT044 | TM140117NT044.MV | DEFLAKED BROKE TO MIXING CHEST CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 6 | %Cs | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD111 |  | TM140117NC044 | TM140117NS044 | TM140117NS044.MV | DEFLAKED BROKE TO MIXING CHEST CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA112 | TM1401ASD112 | TM140117NC044 | TM140117NV044 | TM140117NV044.OUT | DEFLAKED BROKE TO MIXING CHEST CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS046 | TM140117SV046 | TM140117SV046 | BROKE DEFLAKED CHEST OUTLET ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS112 |  | TM140117HS046 | TM140117SV046.ZSC | TM140117SV046.GSC | BROKE DEFLAKED CHEST OUTLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS112 |  | TM140117HS046 | TM140117SV046.ZSO | TM140117SV046.GSO | BROKE DEFLAKED CHEST OUTLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS112 |  | TM140117HS046 | TM140117EV046 | TM140117EV046 | BROKE DEFLAKED CHEST OUTLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS048 | TM140117SV048 | TM140117SV048 | SEALING WATER TO YANKEE PULPER AGITATOR ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS103 |  | TM140117HS048 | TM140117SV048.ZSC | TM140117SV048.GSC | SEALING WATER TO YANKEE PULPER AGITATOR ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS103 |  | TM140117HS048 | TM140117SV048.ZSO | TM140117SV048.GSO | SEALING WATER TO YANKEE PULPER AGITATOR ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS103 |  | TM140117HS048 | TM140117EV048 | TM140117EV048 | SEALING WATER TO YANKEE PULPER AGITATOR ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA112 |  | TM140117PC049 | TM140117PT049 | TM140117PT049.MV | BROKE DEFLAKED CHEST PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 4 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS051 | TM140117SV051 | TM140117SV051 | SEALING WATER TO BROKE DEFLAKER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS203 |  | TM140117HS051 | TM140117SV051.ZSC | TM140117SV051.GSC | SEALING WATER TO BROKE DEFLAKER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS203 |  | TM140117HS051 | TM140117SV051.ZSO | TM140117SV051.GSO | SEALING WATER TO BROKE DEFLAKER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS203 |  | TM140117HS051 | TM140117EV051 | TM140117EV051 | SEALING WATER TO BROKE DEFLAKER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA201 |  | TM140117PI052 | TM140117PT052 | TM140117PT052.MV | BROKE DEFLAKER ACCEPT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD201 |  | TM140117TS053 | TM140117TS053 | TM140117TS053.H | BROKE DEFLAKER OUTLET TEMPERATURE HIGH | TS | Temperature switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [7 empty] | Temp. High | Not Temp. High | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS055 | TM140117SV055 | TM140117SV055 | SHOWER WATER TO YANKEE PULPER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS103 |  | TM140117HS055 | TM140117SV055.ZSC | TM140117SV055.GSC | SHOWER WATER TO YANKEE PULPER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS103 |  | TM140117HS055 | TM140117SV055.ZSO | TM140117SV055.GSO | SHOWER WATER TO YANKEE PULPER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS103 |  | TM140117HS055 | TM140117EV055 | TM140117EV055 | SHOWER WATER TO YANKEE PULPER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1402JBA112 | TM1402ASD113 | TM140117HC056 | TM140117HV056 | TM140117HV056.OUT | BROKE INTERIM TOWER PUMP OUTLET CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117KS057 | TM140117SV057A | TM140117SV057A | BROKE THICKENER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS201 |  | TM140117KS057 | TM140117SV057A.ZSC | TM140117SV057A.GSC | BROKE THICKENER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS201 |  | TM140117KS057 | TM140117SV057A.ZSO | TM140117SV057A.GSO | BROKE THICKENER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS201 |  | TM140117KS057 | TM140117EV057A | TM140117EV057A | BROKE THICKENER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD201 | TM1401ASD201 | TM140117KS057 | TM140117EV057B | TM140117EV057B | BROKE THICKENER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD201 | TM1401ASD201 | TM140117KS057 | TM140117EV057C | TM140117EV057C | BROKE THICKENER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS058 | TM140117SV058 | TM140117SV058 | BROKE THICKENER TANK PUMP INLET ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS101 |  | TM140117HS058 | TM140117SV058.ZSC | TM140117SV058.GSC | BROKE THICKENER TANK PUMP INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS101 |  | TM140117HS058 | TM140117SV058.ZSO | TM140117SV058.GSO | BROKE THICKENER TANK PUMP INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS101 |  | TM140117HS058 | TM140117EV058 | TM140117EV058 | BROKE THICKENER TANK PUMP INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS061 | TM140117SV061 | TM140117SV061 | BROKE DEFLAKED CHEST PUMP OUTLET TO MIXING CHEST ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS112 |  | TM140117HS061 | TM140117SV061.ZSC | TM140117SV061.GSC | BROKE DEFLAKED CHEST PUMP OUTLET TO MIXING CHEST ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS112 |  | TM140117HS061 | TM140117SV061.ZSO | TM140117SV061.GSO | BROKE DEFLAKED CHEST PUMP OUTLET TO MIXING CHEST ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS112 |  | TM140117HS061 | TM140117EV061 | TM140117EV061 | BROKE DEFLAKED CHEST PUMP OUTLET TO MIXING CHEST ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117HS062 | TM140117SV062 | TM140117SV062 | BROKE DEFLAKED CHEST PUMP OUTLET TO BROKE THICKENER TANK ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS112 |  | TM140117HS062 | TM140117SV062.ZSC | TM140117SV062.GSC | BROKE DEFLAKED CHEST PUMP OUTLET TO BROKE THICKENER TANK ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS112 |  | TM140117HS062 | TM140117SV062.ZSO | TM140117SV062.GSO | BROKE DEFLAKED CHEST PUMP OUTLET TO BROKE THICKENER TANK ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBS112 |  | TM140117HS062 | TM140117EV062 | TM140117EV062 | BROKE DEFLAKED CHEST PUMP OUTLET TO BROKE THICKENER TANK ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117NC091 | TM140117NE091 |  | BROKE THICKENER TANK PUMP OUTLET CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230 VAC | [24 empty] | B
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA101 |  | TM140117NC091 | TM140117NT091 | TM140117NT091.MV | BROKE THICKENER TANK PUMP OUTLET CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 6 | %Cs | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD101 |  | TM140117NC091 | TM140117NS091 | TM140117NS091.MV | BROKE THICKENER TANK PUMP OUTLET CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBA101 | TM1401ASD101 | TM140117NC091 | TM140117NV091 | TM140117NV091.OUT | BROKE THICKENER TANK PUMP OUTLET CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD102 |  | TM140117XS093 | TM140117XS093A | TM140117EX008A | SHEET BREAK | XS | Web break signals | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Web break | Not Web break | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD102 |  | TM140117XS093 | TM140117XS093B | TM140117EX008B | SHEET BREAK | XS | Web break signals | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Web break | Not Web break | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD101 |  | TM140117FS095 | TM140117FS095 | TM140117FS095.L | SEALING WATER TO BROKE BROKE THICKENER TANK PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
STOCK APPROACH
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120FC001 | TM140120FE001 |  | NBKP#3 REFINED TOWER #1 PUMP TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS | [27 empty] | B
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 |  | TM140120FC001 | TM140120FT001 | TM140120FT001.MV | NBKP#3 REFINED TOWER #1 PUMP TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1000 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 | TM1401ASD111 | TM140120FC001 | TM140120FV001 | TM140120FV001.OUT | NBKP#3 REFINED TOWER #1 PUMP TO MIXING CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120FC002 | TM140120FE002 |  | LBKP 2 INTERMEDIATE TOWER PUMP TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 |  | TM140120FC002 | TM140120FT002 | TM140120FT002.MV | LBKP 2 INTERMEDIATE TOWER PUMP TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 2700 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 | TM1401ASD111 | TM140120FC002 | TM140120FV002 | TM140120FV002.OUT | LBKP 2 INTERMEDIATE TOWER PUMP TO MIXING CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120FC003 | TM140120FE003 |  | BROKE DEFLAKED CHEST PUMP TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 |  | TM140120FC003 | TM140120FT003 | TM140120FT003.MV | BROKE DEFLAKED CHEST PUMP TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 720 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 | TM1401ASD111 | TM140120FC003 | TM140120FV003 | TM140120FV003.OUT | BROKE DEFLAKED CHEST PUMP TO MIXING CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120FC004 | TM140120FE004 |  | SP2 BROKE TOWER PUMP TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 |  | TM140120FC004 | TM140120FT004 | TM140120FT004.MV | SP2 BROKE TOWER PUMP TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1100 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 | TM1401ASD111 | TM140120FC004 | TM140120FV004 | TM140120FV004.OUT | SP2 BROKE TOWER PUMP TO MIXING CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120FC005 | TM140120FE005 |  | RECOVERED STOCK PUMP TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 |  | TM140120FC005 | TM140120FT005 | TM140120FT005.MV | RECOVERED STOCK PUMP TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1800 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120HS006 | TM140120SV006 | TM140120SV006 | SWEETENER PUMP INLET ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS111 |  | TM140120HS006 | TM140120SV006.ZSC | TM140120SV006.GSC | SWEETENER PUMP INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS111 |  | TM140120HS006 | TM140120SV006.ZSO | TM140120SV006.GSO | SWEETENER PUMP INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS111 |  | TM140120HS006 | TM140120EV006 | TM140120EV006 | SWEETENER PUMP INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 |  | TM140120LC008 | TM140120LT008 | TM140120LT008.MV | MIXING CHEST LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 5000 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120HS009 | TM140120SV009 | TM140120SV009 | DILUTION WATER TO SWEETENER PUMP INLET ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS111 |  | TM140120HS009 | TM140120SV009.ZSC | TM140120SV009.GSC | DILUTION WATER TO SWEETENER PUMP INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS111 |  | TM140120HS009 | TM140120SV009.ZSO | TM140120SV009.GSO | DILUTION WATER TO SWEETENER PUMP INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS111 |  | TM140120HS009 | TM140120EV009 | TM140120EV009 | DILUTION WATER TO SWEETENER PUMP INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD111 |  | TM140120FS010 | TM140120FS010 | TM140120FS010.L | SEALING WATER TO SWEETENER PUMP FLOW | FS | Flow Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120HS011 | TM140120SV011 | TM140120SV011 | MIXING CHEST DISCHAGE ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS111 |  | TM140120HS011 | TM140120SV011.ZSC | TM140120SV011.GSC | MIXING CHEST DISCHAGE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS111 |  | TM140120HS011 | TM140120SV011.ZSO | TM140120SV011.GSO | MIXING CHEST DISCHAGE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS111 |  | TM140120HS011 | TM140120EV011 | TM140120EV011 | MIXING CHEST DISCHAGE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120NC012 | TM140120NE012 |  | MIXING CHEST PUMP OUTLET CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230 VAC | [24 empty] | B
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 |  | TM140120NC012 | TM140120NT012 | TM140120NT012.MV | MIXING CHEST PUMP OUTLET CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 6 | %C | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD111 |  | TM140120NC012 | TM140120NS012 | TM140120NS012.MV | MIXING CHEST PUMP OUTLET CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 | TM1401ASD111 | TM140120NC012 | TM140120NV012 | TM140120NV012.OUT | MIXING CHEST PUMP OUTLET CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD111 |  | TM140120FS014 | TM140120FS014 | TM140120FS014.L | SEALING WATER TO MIXING CHEST PUMP 1 FLOW | FS | Flow Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120FC015 | TM140120FE015 |  | NBKP#3 REFINED TOWER #2 PUMP1 TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS | [27 empty] | B
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 |  | TM140120FC015 | TM140120FT015 | TM140120FT015.MV | NBKP#3 REFINED TOWER #2 PUMP1 TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1000 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 | TM1401ASD111 | TM140120FC015 | TM140120FV015 | TM140120FV015.OUT | NBKP#3 REFINED TOWER #2 PUMP1 TO MIXING CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA201 |  | TM140120PI021 | TM140120PT021 | TM140120PT021.MV | TICKLER REFINER FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120CB01 |  | TM140120PI021 | TM140120PI021 | TM140120PI021.IND | TICKLER REFINER FEED PRESSURE | PI | Local digital indicator | Field | DCS | AO | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA201 |  | TM140120PI022 | TM140120PT022 | TM140120PT022.MV | TICKLER REFINER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120CB01 |  | TM140120PI022 | TM140120PI022 | TM140120PI022.IND | TICKLER REFINER OUTLET PRESSURE | PI | Local digital indicator | Field | DCS | AO | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120HS024 | TM140120SV024 | TM140120SV024 | TICKLER REFINER FEED ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS204 |  | TM140120HS024 | TM140120SV024.ZSC | TM140120SV024.GSC | TICKLER REFINER FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS204 |  | TM140120HS024 | TM140120SV024.ZSO | TM140120SV024.GSO | TICKLER REFINER FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS204 |  | TM140120HS024 | TM140120EV024 | TM140120EV024 | TICKLER REFINER FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120HS025 | TM140120SV025 | TM140120SV025 | TICKLER REFINER ACCEPT ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS204 |  | TM140120HS025 | TM140120SV025.ZSC | TM140120SV025.GSC | TICKLER REFINER ACCEPT ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS204 |  | TM140120HS025 | TM140120SV025.ZSO | TM140120SV025.GSO | TICKLER REFINER ACCEPT ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS204 |  | TM140120HS025 | TM140120EV025 | TM140120EV025 | TICKLER REFINER ACCEPT ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120HS026 | TM140120SV026 | TM140120SV026 | TICKLER REFINER BYPASS ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS204 |  | TM140120HS026 | TM140120SV026.ZSC | TM140120SV026.GSC | TICKLER REFINER BYPASS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS204 |  | TM140120HS026 | TM140120SV026.ZSO | TM140120SV026.GSO | TICKLER REFINER BYPASS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS204 |  | TM140120HS026 | TM140120EV026 | TM140120EV026 | TICKLER REFINER BYPASS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120HS027 | TM140120SV027 | TM140120SV027 | DILUTION WATER TO TICKLER REFINER FEED ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS204 |  | TM140120HS027 | TM140120SV027.ZSC | TM140120SV027.GSC | DILUTION WATER TO TICKLER REFINER FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS204 |  | TM140120HS027 | TM140120SV027.ZSO | TM140120SV027.GSO | DILUTION WATER TO TICKLER REFINER FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS204 |  | TM140120HS027 | TM140120EV027 | TM140120EV027 | DILUTION WATER TO TICKLER REFINER FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120HS028 | TM140120SV028 | TM140120SV028 | SEALING WATER TO TICKLER REFINER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS204 |  | TM140120HS028 | TM140120SV028.ZSC | TM140120SV028.GSC | SEALING WATER TO TICKLER REFINER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS204 |  | TM140120HS028 | TM140120SV028.ZSO | TM140120SV028.GSO | SEALING WATER TO TICKLER REFINER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS204 |  | TM140120HS028 | TM140120EV028 | TM140120EV028 | SEALING WATER TO TICKLER REFINER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD202 |  | TM140120FS029 | TM140120FS029 | TM140120FS029.L | SEALING WATER TO TICKLER REFINER FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120TIZ030 | TM140120TE030 |  | TICKLER REFINER OUTLET TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | B | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA201 |  | TM140120TIZ030 | TM140120TT030 | TM140120TT030.MV | TICKLER REFINER OUTLET TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD202 |  | TM140120TIZ030 | TM140120TS030 | TM140120TS030.H | TICKLER REFINER OUTLET TEMPERATURE HIGH | TS | Temperature switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 150 | ˚C | [7 empty] | Temp. High | Not Temp. High | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD202 |  | TM140120GS031 | TM140120GS031.A | TM140120GS031.A.START | TICKLER REFINER FILLINGS POSITION START | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Start | Start | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD202 |  | TM140120GS031 | TM140120GS031.B | TM140120GS031.B.OPEN | TICKLER REFINER FILLINGS POSITION OPEN | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD202 |  | TM140120GS031 | TM140120GS031.C | TM140120GS031.C.SAF | TICKLER REFINER FILLINGS POSITION SAFETY | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Safety | Safety | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | MCC |  | TM140120EC033 | TM140120ET033 | TM140120ET033.MV | TICKLER REFINER POWER | ET | Power transmitter | MCC | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | MCC | 0 | 355 | kW
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120CB01 |  | TM140120EC033 | TM140120EI033 | TM140120EI033.IND | TICKLER REFINER POWER | EI | Local digital indicator | Field | DCS | AO | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 100 | % | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120FC034 | TM140120FE034 |  | TICKLER REFINER TO MACHINE CHEST FLOW | FE | Magnetic flow Sensor | Field
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 |  | TM140120FC034 | TM140120FT034 | TM140120FT034.MV | TICKLER REFINER TO MACHINE CHEST FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 3600 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 | TM1401ASD111 | TM140120FC034 | TM140120FV034 | TM140120FV034.OUT | TICKLER REFINER TO MACHINE CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120FC035 | TM140120FE035 |  | TICKLER REFINER RECIRCULATION FLOW | FE | Magnetic flow Sensor | Field
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 |  | TM140120FC035 | TM140120FT035 | TM140120FT035.MV | TICKLER REFINER RECIRCULATION FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1800 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 | TM1401ASD111 | TM140120FC035 | TM140120FV035 | TM140120FV035.OUT | TICKLER REFINER RECIRCULATION FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120WC036 | TM140120WX036 | TM140120WX036.SOF | TICKLER REFINER PRODUCTION | WX | DCS software function | DCS | DCS |  | Software function
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120AI037 | TM140120AE037 |  | TICKLER REFINER FREENESS | AE | Freeness sensor | Field
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 |  | TM140120AI037 | TM140120AT037 | TM140120AT037.MV | TICKLER REFINER FREENESS | AT | Freeness transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 15 | 750 | ml CSF | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD111 |  | TM140120AI037 | TM140120AS037 | TM140120AS037.MV | TICKLER REFINER FREENESS | AS | Freeness transmitter Stop Sampling | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120XS038 | TM140120CB01 | TM110011CB01 | TICKLER REFINER CONTROL | CB | Local Control Box | Field |  |  |  | 230 VAC | [24 empty] | 4 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120CB01 |  | TM140120XS038 | TM140120H11 038 | TM140120H11 038.RUN/F | TICKLER REFINER MOTOR RUN / FAULT | H1 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Run | Run | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120CB01 |  | TM140120XS038 | TM140120H21 038 | TM140120H21 038.L/F | TICKLER REFINER LOAD / FAULT | H2 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Load | Load | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120CB01 |  | TM140120XS038 | TM140120H22 038 | TM140120H22 038.REL/F | TICKLER REFINER RELEASE / FAULT | H2 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Release | Release | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120CB01 |  | TM140120XS038 | TM140120H23 038 | TM140120H23 038.FAULT | TICKLER REFINER FAULT | H2 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Fault | Fault | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120CB01 |  | TM140120XS038 | TM140120S10 038 | TM140120S10 038.ESTOP | TICKLER REFINER PANEL E - STOP | S1 | E - Stop Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | E - Stop | Not E - Stop | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120CB01 |  | TM140120XS038 | TM140120S11 038 | TM140120S11 038.START | TICKLER REFINER START | S1 | Illuminated Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Start | Start | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120CB01 |  | TM140120XS038 | TM140120S12 038 | TM140120S12 038.STOP | TICKLER REFINER STOP | S1 | Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Stop | Not Stop | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120CB01 |  | TM140120XS038 | TM140120S20 038 | TM140120S20 038.L/D | OPERATING MODE SELECT SWITCH - LOCAL/DCS | S2 | Select Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | DCS | Local | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120CB01 |  | TM140120XS038 | TM140120S21 038 | TM140120S21 038.LOAD | TICKLER REFINER LOAD | S2 | Illuminated Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Load | Load | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120CB01 |  | TM140120XS038 | TM140120S22 038 | TM140120S22 038.RELEASE | TICKLER REFINER RELEASE | S2 | Illuminated Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Release | Release | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120CB01 |  | TM140120XS038 | TM140120S23 038 | TM140120S23 038.FAST | TICKLER REFINER FAST | S2 | Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Fast | Fast | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120CB01 |  | TM140120XS038 | TM140120S24 038 | TM140120S24 038.TEST | TICKLER REFINER CB LAMP TEST | S2 | Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Lamp Test | Lamp Test | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120EC039 | TM140120EX039 | TM140120EX039.SOF | TICKLER REFINER POWER | EX | DCS software function | DCS | DCS |  | Software function | [25 empty] | B
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 |  | TM140120PC045 | TM140120PT045 | TM140120PT045.MV | SWEETENER PUMP OUTLET OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 |  | TM140120LC051 | TM140120LT051 | TM140120LT051.MV | MACHINE CHEST LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 5000 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120HS052 | TM140120SV052 | TM140120SV052 | MACHINE CHEST DISCHAGE ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS112 |  | TM140120HS052 | TM140120SV052.ZSC | TM140120SV052.GSC | MACHINE CHEST DISCHAGE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS112 |  | TM140120HS052 | TM140120SV052.ZSO | TM140120SV052.GSO | MACHINE CHEST DISCHAGE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS112 |  | TM140120HS052 | TM140120EV052 | TM140120EV052 | MACHINE CHEST DISCHAGE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120NC053 | TM140120NE053 |  | MACHINE CHEST PUMP OUTLET CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230 VAC
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 |  | TM140120NC053 | TM140120NT053 | TM140120NT053.MV | MACHINE CHEST PUMP OUTLET CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 6 | %C | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD111 |  | TM140120NC053 | TM140120NS053 | TM140120NS053.MV | MACHINE CHEST PUMP OUTLET CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 | TM1401ASD111 | TM140120NC053 | TM140120NV053 | TM140120NV053.OUT | MACHINE CHEST PUMP OUTLET CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA111 |  | TM140120PC054 | TM140120PT054 | TM140120PT054.MV | MACHINE CHEST PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120FC055 | TM140120FE055 |  | MACHINE CHEST PUMP OUTLET FLOW | FE | Magnetic flow Sensor | Field
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA102 |  | TM140120FC055 | TM140120FT055 | TM140120FT055.MV | MACHINE CHEST PUMP OUTLET FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 3600 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120FC055 | TM140120FV055 | TM140120FV055.OUT | MACHINE CHEST PUMP OUTLET FLOW CV SETPOINT | FV | Basic Weight Valve | [29 empty] | C
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA102 |  | TM140120FC055 | TM140120FY055 | TM140120FY055.MV | MACHINE CHEST PUMP OUTLET FLOW CV POSITION FEEDBACK | FY | Valve Position Feedback | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD101 |  | TM140120FC055 | TM140120FV055.ZSC | TM140120FV055.GSC | MACHINE CHEST PUMP OUTLET FLOW CV CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD101 |  | TM140120FC055 | TM140120FV055.ZSO | TM140120FV055.GSO | MACHINE CHEST PUMP OUTLET FLOW CV OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD101 |  | TM140120FC055 | TM140120FV055.STP | TM140120FV055.STP | MACHINE CHEST PUMP OUTLET FLOW CV CLOSE COMMAND | STP | Close Command | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [11 empty] | Close | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD101 |  | TM140120FC055 | TM140120FV055.STO | TM140120FV055.STO | MACHINE CHEST PUMP OUTLET FLOW CV OPEN COMMAND | STO | Open Command | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [11 empty] | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD111 |  | TM140120FS057 | TM140120FS057 | TM140120FS057.L | SEALING WATER TO MACHINE CHEST PUMP 1 FLOW | FS | Flow Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA202 |  | TM140120LI061 | TM140120LT061 | TM140120LT061.MV | SILO LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3000 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120HS062 | TM140120SV062 | TM140120SV062 | WHITE WATER TO SILO ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS205 |  | TM140120HS062 | TM140120SV062.ZSC | TM140120SV062.GSC | WHITE WATER TO SILO ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS205 |  | TM140120HS062 | TM140120SV062.ZSO | TM140120SV062.GSO | WHITE WATER TO SILO ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS205 |  | TM140120HS062 | TM140120EV062 | TM140120EV062 | WHITE WATER TO SILO ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140135TC020 | TM140135TE020 |  | SILO TEMPERATURE | TE | Temperature Sensor | Field
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA202 |  | TM140135TC020 | TM140135TT020 | TM140135TT020.MV | SILO TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA202 | TM1401ASD201 | TM140135TC020 | TM140135TV020 | TM140135TV020.OUT | SILO TEMPERATURE CV SETPOINT | TV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120AI064 | TM140120AE064 |  | SILO CHANNEL OVERFLOW PARTICLE CHARGE DETECT | AE | PCD sensor | Field | DCS
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA202 |  | TM140120AI064 | TM140120AT064 | TM140120AT064.MV | SILO CHANNEL OVERFLOW PARTICLE CHARGE DETECT | AT | PCD transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | -150 | -30 | µEQ/l | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD202 |  | TM140120AI064 | TM140120AS064 | TM140120AS064.INT | SILO CHANNEL OVERFLOW PARTICLE CHARGE INTERLOCK | AS | PCD transmitter Stop Sampling | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120AC065 | TM140120AE065 |  | SILO PH | AE | pH Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA202 |  | TM140120AC065 | TM140120AT065 | TM140120AT065.MV | SILO PH | AT | pH Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 14 | Ph | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120HS066 | TM140120SV066 | TM140120SV066 | MACHINE CHEST PUMP OUTLET TO SILO ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 0
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS102 |  | TM140120HS066 | TM140120SV066.ZSC | TM140120SV066.GSC | MACHINE CHEST PUMP OUTLET TO SILO ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS102 |  | TM140120HS066 | TM140120SV066.ZSO | TM140120SV066.GSO | MACHINE CHEST PUMP OUTLET TO SILO ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS102 |  | TM140120HS066 | TM140120EV066 | TM140120EV066 | MACHINE CHEST PUMP OUTLET TO SILO ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120HS067 | TM140120SV067 | TM140120SV067 | MACHINE CHEST PUMP OUTLET TO RECOVERED STOCK CHEST ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 0
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS102 |  | TM140120HS067 | TM140120SV067.ZSC | TM140120SV067.GSC | MACHINE CHEST PUMP OUTLET TO RECOVERED STOCK CHEST ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS102 |  | TM140120HS067 | TM140120SV067.ZSO | TM140120SV067.GSO | MACHINE CHEST PUMP OUTLET TO RECOVERED STOCK CHEST ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS102 |  | TM140120HS067 | TM140120EV067 | TM140120EV067 | MACHINE CHEST PUMP OUTLET TO RECOVERED STOCK CHEST ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120HS072 | TM140120SV072 | TM140120SV072 | SEALING WATER TO FAN PUMP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS101 |  | TM140120HS072 | TM140120SV072.ZSC | TM140120SV072.GSC | SEALING WATER TO FAN PUMP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS101 |  | TM140120HS072 | TM140120SV072.ZSO | TM140120SV072.GSO | SEALING WATER TO FAN PUMP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS101 |  | TM140120HS072 | TM140120EV072 | TM140120EV072 | SEALING WATER TO FAN PUMP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD101 |  | TM140120FS073 | TM140120FS073 | TM140120FS073.L | SEALING WATER TO FAN PUMP FLOW L A | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120HS075 | TM140120SV075 | TM140120SV075 | FAN PUMP OUTLET ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS101 |  | TM140120HS075 | TM140120SV075.ZSC | TM140120SV075.GSC | FAN PUMP OUTLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS101 |  | TM140120HS075 | TM140120SV075.ZSO | TM140120SV075.GSO | FAN PUMP OUTLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS101 |  | TM140120HS075 | TM140120EV075 | TM140120EV075 | FAN PUMP OUTLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA102 | TM1401ASD102 | TM140120HC078 | TM140120HV078 | TM140120HV078.OUT | 1ST STAGE APPROACH SCREEN REJECT CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120XI079 | TM140120XE079 |  | 1ST STAGE APPROACH SCREEN MOTOR VIBRATION 1 | XE | Vibration sensor | Field | [28 empty] | C | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA102 |  | TM140120XI079 | TM140120XT079 | TM140120XT079.MV | 1ST STAGE APPROACH SCREEN MOTOR VIBRATION 1 | XT | Vibration transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | [22 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA102 |  | TM140120PI081 | TM140120PT081 | TM140120PT081.MV | 1ST STAGE APPROACH SCREEN FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA102 |  | TM140120PI082 | TM140120PT082 | TM140120PT082.MV | 1ST STAGE APPROACH SCREEN ACCEPT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120PDI083 | TM140120PDX083 | TM140120PDX083.SOF | 1ST STAGE APPROACH SCREEN DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120FI084 | TM140120FE084 |  | 1ST STAGE APPROACH SCREEN REJECT FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | B
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA102 |  | TM140120FI084 | TM140120FT084 | TM140120FT084.MV | 1ST STAGE APPROACH SCREEN REJECT FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 2000 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120HS085 | TM140120SV085 | TM140120SV085 | FROM 1ST STAGE APPROACH SCREENTO SILO CHANNEL ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS101 |  | TM140120HS085 | TM140120SV085.ZSC | TM140120SV085.GSC | FROM 1ST STAGE APPROACH SCREENTO SILO CHANNEL ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS101 |  | TM140120HS085 | TM140120SV085.ZSO | TM140120SV085.GSO | FROM 1ST STAGE APPROACH SCREENTO SILO CHANNEL ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS101 |  | TM140120HS085 | TM140120EV085 | TM140120EV085 | FROM 1ST STAGE APPROACH SCREENTO SILO CHANNEL ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120HS086 | TM140120SV086 | TM140120SV086 | SEALING WATER TO 1ST STAGE APPROACH SCREEN ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS101 |  | TM140120HS086 | TM140120SV086.ZSC | TM140120SV086.GSC | SEALING WATER TO 1ST STAGE APPROACH SCREEN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS101 |  | TM140120HS086 | TM140120SV086.ZSO | TM140120SV086.GSO | SEALING WATER TO 1ST STAGE APPROACH SCREEN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS101 |  | TM140120HS086 | TM140120EV086 | TM140120EV086 | SEALING WATER TO 1ST STAGE APPROACH SCREEN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD101 |  | TM140120FS087 | TM140120FS087 | TM140120FS087.L | SEALING WATER TO 1ST STAGE APPROACH SCREEN FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA201 |  | TM140120PI091 | TM140120PT091 | TM140120PT091.MV | 2ND STAGE APPROACH SCREEN FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA201 |  | TM140120PI092 | TM140120PT092 | TM140120PT092.MV | 2ND STAGE APPROACH SCREEN ACCEPT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120PDI093 | TM140120PDX093 | TM140120PDX093.SOF | 2ND STAGE APPROACH SCREEN DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120KC094 | TM140120SV094 | TM140120SV094 | 2ND STAGE APPROACH SCREEN REJECT ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD202 |  | TM140120KC094 | TM140120SV094.ZSC | TM140120SV094.GSC | 2ND STAGE APPROACH SCREEN REJECT ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD202 |  | TM140120KC094 | TM140120SV094.ZSO | TM140120SV094.GSO | 2ND STAGE APPROACH SCREEN REJECT ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD202 | TM1401ASD201 | TM140120KC094 | TM140120EV094 | TM140120EV094 | 2ND STAGE APPROACH SCREEN REJECT ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA201 | TM1401ASD201 | TM140120HC095 | TM140120HV095 | TM140120HV095.OUT | FROM 2ND STAGE APPROACH SCREEN TO SILO CHANNEL CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120HS096 | TM140120SV096 | TM140120SV096 | SEALING WATER TO 2ND STAGE APPROACH SCREEN ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS203 |  | TM140120HS096 | TM140120SV096.ZSC | TM140120SV096.GSC | SEALING WATER TO 2ND STAGE APPROACH SCREEN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS203 |  | TM140120HS096 | TM140120SV096.ZSO | TM140120SV096.GSO | SEALING WATER TO 2ND STAGE APPROACH SCREEN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBS203 |  | TM140120HS096 | TM140120EV096 | TM140120EV096 | SEALING WATER TO 2ND STAGE APPROACH SCREEN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBD202 |  | TM140120FS097 | TM140120FS097 | TM140120FS097.L | SEALING WATER TO 2ND STAGE APPROACH SCREEN FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA102 |  | TM140120LC101 | TM140120LT101 | TM140120LT101.MV | WIRE WHITE WATER TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3300 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA102 | TM1401ASD102 | TM140120HC103 | TM140120HV103 | TM140120HV103.OUT | W.W OVERFLOW CHEST PUMP TO SILO CHANNEL CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA102 | TM1401ASD102 | TM140120HC104 | TM140120HV104 | TM140120HV104.OUT | W.W OVERFLOW CHEST PUMP TO W.W COLLECTION TANK CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120XI106 | TM140120XE106 |  | 1ST STAGE APPROACH SCREEN MOTOR VIBRATION 2 | XE | Vibration sensor | Field | [28 empty] | C | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA102 |  | TM140120XI106 | TM140120XT106 | TM140120XT106.MV | 1ST STAGE APPROACH SCREEN MOTOR VIBRATION 2 | XT | Vibration transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | [22 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA202 |  | TM140120PC111 | TM140120PT111 | TM140120PT111.MV | HEADBOX PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA102 | TM1401ASD102 | TM140120HC112 | TM140120HV112 | TM140120HV112.OUT | HEADBOX RECIRCULATION CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140120 |  |  | TM140120FI114 | TM140120FE114 |  | HEADBOX RECIRCULATION FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | B
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM1401JBA102 |  | TM140120FI114 | TM140120FT114 | TM140120FT114.MV | HEADBOX RECIRCULATION FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 5000 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140115 |  |  | TM140115FC005 | TM140115FE005 |  | WET STRENGHT AGENT TO MIXING CHEST PUMP FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3001 | TM140115 | TM1401JBA111 |  | TM140115FC005 | TM140115FT005 | TM140115FT005.MV | WET STRENGHT AGENT TO MIXING CHEST PUMP FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | hold | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140115 |  |  | TM140115FC006 | TM140115FE006 |  | DRY STRENGHT AGENT TO MACHINE CHEST PUMP FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3001 | TM140115 | TM1401JBA111 |  | TM140115FC006 | TM140115FT006 | TM140115FT006.MV | DRY STRENGHT AGENT TO MACHINE CHEST PUMP FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | hold | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140115 |  |  | TM140115FC007 | TM140115FE007 |  | SOFT AGENT TO MIXING CHEST PUMP FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3001 | TM140115 | TM1401JBA111 |  | TM140115FC007 | TM140115FT007 | TM140115FT007.MV | SOFT AGENT TO MIXING CHEST PUMP FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | hold | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140115 |  |  | TM140115FC008 | TM140115FE008 |  | CMC TO FAN PUMP FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3001 | TM140115 | TM1401JBA102 |  | TM140115FC008 | TM140115FT008 | TM140115FT008.MV | CMC TO FAN PUMP FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | hold | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140115 |  |  | TM140115HS069 | TM140115SV069 | TM140115SV069 | WET STRENGHT AGENT TO MIXING CHEST PUMP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3001 | TM140115 | TM1401JBS111 |  | TM140115HS069 | TM140115SV069.ZSC | TM140115SV069.GSC | WET STRENGHT AGENT TO MIXING CHEST PUMP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140115 | TM1401JBS111 |  | TM140115HS069 | TM140115SV069.ZSO | TM140115SV069.GSO | WET STRENGHT AGENT TO MIXING CHEST PUMP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140115 | TM1401JBS111 |  | TM140115HS069 | TM140115EV069 | TM140115EV069 | WET STRENGHT AGENT TO MIXING CHEST PUMP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140115 |  |  | TM140115HS070 | TM140115SV070 | TM140115SV070 | DRY STRENGHT AGENT TO MACHINE CHEST PUMP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3001 | TM140115 | TM1401JBS112 |  | TM140115HS070 | TM140115SV070.ZSC | TM140115SV070.GSC | DRY STRENGHT AGENT TO MACHINE CHEST PUMP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140115 | TM1401JBS112 |  | TM140115HS070 | TM140115SV070.ZSO | TM140115SV070.GSO | DRY STRENGHT AGENT TO MACHINE CHEST PUMP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140115 | TM1401JBS112 |  | TM140115HS070 | TM140115EV070 | TM140115EV070 | DRY STRENGHT AGENT TO MACHINE CHEST PUMP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140115 |  |  | TM140115HS071 | TM140115SV071 | TM140115SV071 | SOFT AGENT TO MIXING CHEST PUMP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3001 | TM140115 | TM1401JBS111 |  | TM140115HS071 | TM140115SV071.ZSC | TM140115SV071.GSC | SOFT AGENT TO MIXING CHEST PUMP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140115 | TM1401JBS111 |  | TM140115HS071 | TM140115SV071.ZSO | TM140115SV071.GSO | SOFT AGENT TO MIXING CHEST PUMP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140115 | TM1401JBS111 |  | TM140115HS071 | TM140115EV071 | TM140115EV071 | SOFT AGENT TO MIXING CHEST PUMP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140115 |  |  | TM140115HS072 | TM140115SV072 | TM140115SV072 | CMC TO FAN PUMP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3001 | TM140115 | TM1401JBS101 |  | TM140115HS072 | TM140115SV072.ZSC | TM140115SV072.GSC | CMC TO FAN PUMP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140115 | TM1401JBS101 |  | TM140115HS072 | TM140115SV072.ZSO | TM140115SV072.GSO | CMC TO FAN PUMP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3001 | TM140115 | TM1401JBS101 |  | TM140115HS072 | TM140115EV072 | TM140115EV072 | CMC TO FAN PUMP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
WHITE WATER AND FIBRE RECOVERY
P-OKITM07-10-320-07-PID-3005 | TM140121 |  |  | TM140121FC001 | TM140121FE001 |  | W.W TO DISC FILTER FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA112 |  | TM140121FC001 | TM140121FT001 | TM140121FT001.MV | W.W TO DISC FILTER FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 5000 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA112 | TM1401ASD112 | TM140121FC001 | TM140121FV001 | TM140121FV001.OUT | W.W TO DISC FILTER FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 |  | TM140121LC002 | TM140121LT002 | TM140121LT002.MV | SUPER CLARIFIED TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 | TM1401ASD101 | TM140121LC002 | TM140121LV002 | TM140121LV002.OUT | SUPER CLARIFIED TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 |  |  | TM140121FFC003 | TM140121FE003 |  | SWEETENER STOCK FLOW | FE | Magnetic flow Sensor | Field
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA112 |  | TM140121FFC003 | TM140121FT003 | TM140121FT003.MV | SWEETENER STOCK FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1800 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA112 | TM1401ASD112 | TM140121FFC003 | TM140121FV003 | TM140121FV003.OUT | SWEETENER STOCK FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 |  | TM140121LC004 | TM140121LT004 | TM140121LT004.MV | CLARIFIED TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 | TM1401ASD101 | TM140121LC004 | TM140121LV004 | TM140121LV004.OUT | CLARIFIED TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 |  | TM140121LC005 | TM140121LT005 | TM140121LT005.MV | CLOUDY FILTRATE TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3300 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 | TM1401ASD101 | TM140121LC005 | TM140121LV005 | TM140121LV005.OUT | CLOUDY FILTRATE TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 |  | TM140121LC006 | TM140121LT006 | TM140121LT006.MV | RECOVERED STOCK CHEST LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA112 |  | TM140121LC007 | TM140121LT007 | TM140121LT007.MV | W.W. COLLECTION TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10000 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA112 | TM1401ASD112 | TM140121LC007 | TM140121LV007A | TM140121LV007A.OUT | W.W. COLLECTION TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA112 | TM1401ASD112 | TM140121LC007 | TM140121LV007B | TM140121LV007B.PRO | W.W. COLLECTION TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 |  | TM140121PI008 | TM140121PT008 | TM140121PT008.MV | CWW LP SHOWER FILTER INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 |  |  | TM140121PDI009 | TM140121PDX009 | TM140121PDX009.SOF | CWW LP SHOWER FILTER DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function |  |  |  | 0 | 2 | Bar.g | [19 empty] | B
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 |  | TM140121PC010 | TM140121PT010 | TM140121PT010.MV | CWW LP SHOWER FILTER FILTER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 |  |  | TM140121HS011 | TM140121SV011 | TM140121SV011 | W.W TO DISC FILTER SHOWERS ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBS201 |  | TM140121HS011 | TM140121SV011.ZSC | TM140121SV011.GSC | W.W TO DISC FILTER SHOWERS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBS201 |  | TM140121HS011 | TM140121SV011.ZSO | TM140121SV011.GSO | W.W TO DISC FILTER SHOWERS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBS201 |  | TM140121HS011 | TM140121EV011 | TM140121EV011 | W.W TO DISC FILTER SHOWERS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | MCC |  | TM140121EI012 | TM140121ET012 | TM140121ET012.MV | DISC FILTER TORQUE | ET | Power transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA201 |  | TM140121PI013 | TM140121PT013 | TM140121PT013.MV | DISC FILTER VACUUM | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBD201 |  | TM140121SS014 | TM140121GS014A | TM140121GS014A.SEC | DISC FILTER SECTOR COUNTER SECTOR PULSE | GS | Proximity Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Sector Pulse | Sector Pulse | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBD201 |  | TM140121SS014 | TM140121GS014B | TM140121GS014B.ROT | DISC FILTER SECTOR COUNTER ROTATION PULSE | GS | Proximity Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Rotation Pulse | Rotation Pulse | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBD201 |  | TM140121SS015 | TM140121SS015 | TM140121SS015.L | DISC FILTER SPEED REPULPER SPEED LOW | SS | Speed Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Speed Low | Not Speed Low | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBD201 |  | TM140121XS016 | TM140121S9 016 | TM140121S9 016.DCS/LOCAL | DISC FILTER LOCAL OPERATION MAINDRIVE DCS/LOCAL | S9 | Selector Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Jog | Jog | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBD201 |  | TM140121XS016 | TM140121S11 016 | TM140121S11 016.JOG | DISC FILTER LOCAL OPERATION MAINDRIVE JOG FORWARD | S11 | Push button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Local | DCS | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBD201 |  | TM140121XS017 | TM140121S9 017 | TM140121S9 017.JOG | DISC FILTER LOCAL OPERATION SHOWER OSCILLATION DCS/LOCAL | S9 | Selector Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Jog | Jog | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBD201 |  | TM140121XS017 | TM140121S11 017 | TM140121S11 017.DCS/LOCAL | DISC FILTER LOCAL OPERATION SHOWER OSCILLATION LOCAL START | S11 | Push button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Local | DCS | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 |  | TM140121PI018 | TM140121PT018 | TM140121PT018.MV | SCWW SHOWER FILTER INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 7 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 |  |  | TM140121PDI019 | TM140121PDX019 | TM140121PDX019.SOF | SCWW SHOWER FILTER DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function |  |  |  | 0 | 2 | Bar.g | [19 empty] | B
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 |  | TM140121PC020 | TM140121PT020 | TM140121PT020.MV | SCWW SHOWER FILTER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 7 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA201 |  | TM140121LC021 | TM140121LT021 | TM140121LT021.MV | DISC FILTER LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 2000 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA112 |  | TM140121PC022 | TM140121PT022 | TM140121PT022.MV | TM AREA CRC PUMP OUTLET WHITE WATER PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 7 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 |  | TM140121PI024 | TM140121PT024 | TM140121PT024.MV | CWW HP SHOWER FILTER FILTER INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 25 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 |  |  | TM140121PDI025 | TM140121PDX025 | TM140121PDX025.SOF | CWW HP SHOWER FILTER DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function |  |  |  | 0 | 2 | Bar.g | [19 empty] | B
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 |  | TM140121PC026 | TM140121PT026 | TM140121PT026.MV | CWW HP SHOWER FILTER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 25 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBD201 |  | TM140121XS028 | TM140121S10 028 | TM140121S10 028.ESTOP | DISC FILTER LOCAL OPERATION MAINDRIVE E-STOP | S10 | E - Stop Push Button | +CP01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | E-Stop | [11 empty] | 4 | Andritz
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121CP01 |  | TM140121XS031 | TM140121S1.031 | TM140121S1.031 | CWW LP SHOWER FILTER LOCAL PANEL | S1 | Differential Pressure High alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121CP01 |  | TM140121XS031 | TM140121S2.031 | TM140121S2.031 | CWW LP SHOWER FILTER LOCAL PANEL | S2 | Flush alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121CP01 |  | TM140121XS031 | TM140121S3.031 | TM140121S3.031 | CWW LP SHOWER FILTER LOCAL PANEL | S3 | Power Failure alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121CP02 |  | TM140121XS032 | TM140121S1.032 | TM140121S1.032 | CWW HP SHOWER FILTER LOCAL PANEL | S1 | Differential Pressure High alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121CP02 |  | TM140121XS032 | TM140121S2.032 | TM140121S2.032 | CWW HP SHOWER FILTER LOCAL PANEL | S2 | Flush alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121CP02 |  | TM140121XS032 | TM140121S3.032 | TM140121S3.032 | CWW HP SHOWER FILTER LOCAL PANEL | S3 | Power Failure alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121CP03 |  | TM140121XS033 | TM140121S1.033 | TM140121S1.033 | SCWW SHOWER FILTER LOCAL PANEL | S1 | Differential Pressure High alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121CP03 |  | TM140121XS033 | TM140121S2.033 | TM140121S2.033 | SCWW SHOWER FILTER LOCAL PANEL | S2 | Flush alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121CP03 |  | TM140121XS033 | TM140121S3.033 | TM140121S3.033 | SCWW SHOWER FILTER LOCAL PANEL | S3 | Power Failure alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3005 | TM140121 |  |  | TM140121HS036 | TM140121SV036 | TM140121SV036 | W.W TO DISC FILTER SHOWERS ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBS201 |  | TM140121HS036 | TM140121SV036.ZSC | TM140121SV036.GSC | W.W TO DISC FILTER SHOWERS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBS201 |  | TM140121HS036 | TM140121SV036.ZSO | TM140121SV036.GSO | W.W TO DISC FILTER SHOWERS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBS201 |  | TM140121HS036 | TM140121EV036 | TM140121EV036 | W.W TO DISC FILTER SHOWERS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 |  |  | TM140121FC037 | TM140121FE037 |  | W.W TO DISC FILTER REPULPER FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA201 |  | TM140121FC037 | TM140121FT037 | TM140121FT037.MV | W.W TO DISC FILTER REPULPER FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1000 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA201 | TM1401ASD201 | TM140121FC037 | TM140121FV037 | TM140121FV037.OUT | W.W TO DISC FILTER REPULPER FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA201 |  | TM140121PC038 | TM140121PT038 | TM140121PT038.MV | DISC FILTER SHOWERS PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 | TM1401ASD101 | TM140121HC039 | TM140121HV039 | TM140121HV039.OUT | FRESH WATER TO CLOUDY FILTRATE TANK CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBD101 |  | TM140121FS040 | TM140121FS040 | TM140121FS040.L | SEALING WATER TO REC PULP CHEST PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA201 |  | TM140121PI041 | TM140121PT041 | TM140121PT041.MV | W.W TO DISC FILTER SHOWERS PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 |  |  | TM140121HS045 | TM140121SV045 | TM140121SV045 | REC PULP CHEST PUMP OUTLET TO BROKE INTERIM TOWER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBS111 |  | TM140121HS045 | TM140121SV045.ZSC | TM140121SV045.GSC | REC PULP CHEST PUMP OUTLET TO BROKE INTERIM TOWER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBS111 |  | TM140121HS045 | TM140121SV045.ZSO | TM140121SV045.GSO | REC PULP CHEST PUMP OUTLET TO BROKE INTERIM TOWER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBS111 |  | TM140121HS045 | TM140121EV045 | TM140121EV045 | REC PULP CHEST PUMP OUTLET TO BROKE INTERIM TOWER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 |  |  | TM140121HS046 | TM140121SV046 | TM140121SV046 | REC PULP CHEST PUMP OUTLET TO TM 14.1 MIXING CHEST ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBS111 |  | TM140121HS046 | TM140121SV046.ZSC | TM140121SV046.GSC | REC PULP CHEST PUMP OUTLET TO TM 14.1 MIXING CHEST ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBS111 |  | TM140121HS046 | TM140121SV046.ZSO | TM140121SV046.GSO | REC PULP CHEST PUMP OUTLET TO TM 14.1 MIXING CHEST ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBS111 |  | TM140121HS046 | TM140121EV046 | TM140121EV046 | REC PULP CHEST PUMP OUTLET TO TM 14.1 MIXING CHEST ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 |  | TM140121PC050 | TM140121PT050 | TM140121PT050.MV | CLOUDY CIRCULATION PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA112 |  | TM140121PC136 | TM140121PT136 | TM140121PT136.MV | YANKEE-TRIM PULPER & OVER FLOW PUMP WHITE WATER PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 |  |  | TM140121HS137 | TM140121SV137 | TM140121SV137 | PULP FROM RECOVERED STOCK CHEST ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBS101 |  | TM140121HS137 | TM140121SV137.ZSC | TM140121SV137.GSC | PULP FROM RECOVERED STOCK CHEST ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBS101 |  | TM140121HS137 | TM140121SV137.ZSO | TM140121SV137.GSO | PULP FROM RECOVERED STOCK CHEST ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBS101 |  | TM140121HS137 | TM140121EV137 | TM140121EV137 | PULP FROM RECOVERED STOCK CHEST ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 |  |  | TM140121NC138 | TM140121NE138 |  | REC PULP CHEST PUMP OUTLET CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230 VAC | [24 empty] | B
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 |  | TM140121NC138 | TM140121NT138 | TM140121NT138.MV | REC PULP CHEST PUMP OUTLET CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 6 | %C | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBD101 |  | TM140121NC138 | TM140121NS138 | TM140121NS138.MV | REC PULP CHEST PUMP OUTLET CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 | TM1401ASD101 | TM140121NC138 | TM140121NV138 | TM140121NV138.OUT | REC PULP CHEST PUMP OUTLET CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 |  | TM140121PC140 | TM140121PT140 | TM140121PT140.MV | PMP DEMAND & CLEANING PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 |  | TM140121PC141 | TM140121PT141 | TM140121PT141.MV | SCWW HP SHOWER PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 40 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA111 |  | TM140121FI144 | TM140121FT144 | TM140121FT144.MV | WASTE WATER FROM TM14.1 FLOW | FT | Open channel flow transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 250 | m3/hr | [19 empty] | 1
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 |  | TM140121PC146 | TM140121PT146 | TM140121PT146.MV | DUST SCWW PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 40 | Bar.g | [19 empty] | 4
VACUUM SYSTEM
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123LC014 | TM140123LT014 | TM110123LT014.MV | VACUUM WW TANK LEVEL | LT | DP Level Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 2500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 | TM1401ASD103 | TM140123LC014 | TM140123LV014 | TM140123LV014.OUT | VACUUM WW TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 | TM1401ASD103 | TM140123HC015 | TM140123HV015 | TM140123HV015.OUT | COOLING TOWER OUTLET BYPASS CV SETPOINT | HV | Control Valve | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBD102 |  | TM140123PS021 | TM140123PS021 | TM140123PS021.L | VACUUM PUMP 1 GEAR REDUCER LUBRICATION OIL PRESSURE | PS | Pressure switch | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBD102 |  | TM140123PS022 | TM140123PS022 | TM140123PS022.L | VACUUM PUMP 2 GEAR REDUCER LUBRICATION OIL PRESSURE | PS | Pressure switch | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123FI065 | TM140123FE065 |  | MAKE-UP WATER VACUUM SYSTEM FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123FI065 | TM140123FT065 | TM140123FT065.MV | MAKE-UP WATER VACUUM SYSTEM FLOW | FT | Magnetic flow transmitter | Field | DCS |  | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 720 | l / min | [19 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123TI066 | TM140123TE066 |  | COOLED SEAL WATER TEMPERATURE | TE | Temperature sensor | Field | [28 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123TI066 | TM140123TT066 | TM140123TT066.MV | COOLED SEAL WATER TEMPERATURE | TT | Temperature transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [19 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123PC067 | TM140123PT067 | TM140123PT067.MV | SEAL WATER TO VACUUM PUMPS PRESSURE | PT | Pressure Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 4 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 | TM1401ASD103 | TM140123PC067 | TM140123PV067 | TM140123PV067.OUT | SEAL WATER TO VACUUM PUMPS PRESSURE CV SETPOINT | PV | Control Valve | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123PI073 | TM140123PT073 | TM140123PT073.MV | VACUUM PUMP 1 PRESSURE | PT | Pressure Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123PI074 | TM140123PT074 | TM140123PT074.MV | VACUUM PUMP 1 PRESSURE | PT | Pressure Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123PI075 | TM140123PT075 | TM140123PT075.MV | VACUUM PUMP 2 PRESSURE | PT | Pressure Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123PI076 | TM140123PT076 | TM140123PT076.MV | VACUUM PUMP 2 PRESSURE | PT | Pressure Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123TI079 | TM140123TE079 |  | COOLING TOWER PUMP 2 OUTLET TEMPERATURE | TE | Temperature sensor | Field | [28 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123TI079 | TM140123TT079 | TM140123TT079.MV | COOLING TOWER PUMP 2 OUTLET TEMPERATURE | TT | Temperature transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [19 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123HS081 | TM140123SV081 | TM140123SV081 | VACUUM PUMP 1 DRAIN ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS081 | TM140123SV081.ZSC | TM140123SV081.GSC | VACUUM PUMP 1 DRAIN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS081 | TM140123SV081.ZSO | TM140123SV081.GSO | VACUUM PUMP 1 DRAIN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS081 | TM140123EV081 | TM140123EV081 | VACUUM PUMP 1 DRAIN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123HS083 | TM140123SV083 | TM140123SV083 | VACUUM PUMP 2 DRAIN ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS083 | TM140123SV083.ZSC | TM140123SV083.GSC | VACUUM PUMP 2 DRAIN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS083 | TM140123SV083.ZSO | TM140123SV083.GSO | VACUUM PUMP 2 DRAIN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS083 | TM140123EV083 | TM140123EV083 | VACUUM PUMP 2 DRAIN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123HS091 | TM140123SV091 | TM140123SV091 | VACUUM PUMP 1 COOLING WATER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS091 | TM140123SV091.ZSC | TM140123SV091.GSC | VACUUM PUMP 1 COOLING WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS091 | TM140123SV091.ZSO | TM140123SV091.GSO | VACUUM PUMP 1 COOLING WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS091 | TM140123EV091 | TM140123EV091 | VACUUM PUMP 1 COOLING WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123FI092 | TM140123FE092 |  | COOLING WATER TO VACUUM PUMP 1 FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123FI092 | TM140123FT092 | TM140123FT092.MV | COOLING WATER TO VACUUM PUMP 1 FLOW | FT | Magnetic flow transmitter | Field | DCS |  | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 430 | l / min | [19 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123HS093 | TM140123SV093 | TM140123SV093 | VACUUM PUMP 2 COOLING WATER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS093 | TM140123SV093.ZSC | TM140123SV093.GSC | VACUUM PUMP 2 COOLING WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS093 | TM140123SV093.ZSO | TM140123SV093.GSO | VACUUM PUMP 2 COOLING WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS093 | TM140123EV093 | TM140123EV093 | VACUUM PUMP 2 COOLING WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123FI094 | TM140123FE094 |  | COOLING WATER TO VACUUM PUMP 2 FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123FI094 | TM140123FT094 | TM140123FT094.MV | COOLING WATER TO VACUUM PUMP 2 FLOW | FT | Magnetic flow transmitter | Field | DCS |  | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 420 | l / min | [19 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123LIS095 | TM140123LT095 | TM140123LT095.MV | VACUUM W.W PIT LEVEL | LT | Radar Level Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | mm |  | 10% | 15% | [16 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 | TM1401ASD103 | TM140123HC096 | TM140123HV096 | TM140123HV096.OUT | COOLING TOWER PUMP OUTLET TO COOLING TOWER CV SETPOINT | HV | Control Valve | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 | TM1401ASD103 | TM140123HC097 | TM140123HV097 | TM140123HV097.OUT | COOLING TOWER PUMP OUTLET TO WIRE WHITE WATER TANK CV SETPOINT | HV | Control Valve | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123HS101 | TM140123SV101 | TM140123SV101 | VACUUM SHEAVE ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS101 | TM140123SV101.ZSC | TM140123SV101.GSC | VACUUM SHEAVE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS101 | TM140123SV101.ZSO | TM140123SV101.GSO | VACUUM SHEAVE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS101 | TM140123EV101 | TM140123EV101 | VACUUM SHEAVE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123PI110 | TM140123PT110 | TM140123PT110.MV | VACUUM PUMP INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 3 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123HC113 | TM140123HV113 | TM140123HV113.OUT | ANTI-SURGE ELECTRIC BUTTERFLY VALVE FEEDBACK | HV | Control Valve | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123HC113 | TM140123HV113 | TM140123HV113.OUT | ANTI-SURGE ELECTRIC BUTTERFLY VALVE CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123LIC114 | TM140123LT114 | TM140123LT114.MV | VACUUM SEPARATOR LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM1401JBA101 | TM1401ASD103 | TM140123LIC114 | TM140123LV114 | TM140123LV114.OUT | VACUUM SEPARATOR LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123TISA121 | TM140123TE121 |  | FRONT BEARING TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123TISA121 | TM140123TT121 | TM140123TT121.MV | FRONT BEARING TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123TISA122 | TM140123TE122 |  | REAR BEARING TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123TISA122 | TM140123TT122 | TM140123TT122.MV | REAR BEARING TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123TISA123 | TM140123TE123 |  | THRUST BEARING TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123TISA123 | TM140123TT123 | TM140123TT123.MV | THRUST BEARING TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123TISA124 | TM140123TE124 |  | TEMPERATURE OF STATOR WINDING U | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123TISA124 | TM140123TT124 | TM140123TT124.MV | TEMPERATURE OF STATOR WINDING U | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123TISA125 | TM140123TE125 |  | TEMPERATURE OF STATOR WINDING V | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123TISA125 | TM140123TT125 | TM140123TT125.MV | TEMPERATURE OF STATOR WINDING V | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123TISA126 | TM140123TE126 |  | TEMPERATURE OF STATOR WINDING W | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123TISA126 | TM140123TT126 | TM140123TT126.MV | TEMPERATURE OF STATOR WINDING W | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123XISA127 | TM140123XT127 |  | THE OUTPUT SHAFT VIBRATES IN THE X DIRECTION | XT | Vibration sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123XISA127 | TM140123XT127 | TM140123XT127.MV | THE OUTPUT SHAFT VIBRATES IN THE X DIRECTION | XT | Vibration transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | mm | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123XISA128 | TM140123XT128 |  | THE OUTPUT SHAFT VIBRATES IN THE Y DIRECTION | XT | Vibration sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123XISA128 | TM140123XT128 | TM140123XT128.MV | THE OUTPUT SHAFT VIBRATES IN THE Y DIRECTION | XT | Vibration transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | mm | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123TISA131 | TM140123TE131 |  | OIL SUPPLY OIL TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123TISA131 | TM140123TT131 | TM140123TT131.MV | OIL SUPPLY OIL TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123TISA132 | TM140123TE132 |  | TANK OIL TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123TISA132 | TM140123TT132 | TM140123TT132.MV | TANK OIL TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123PC133 | TM140123PT133 | TM140123PT133.MV | OIL SUPPLY PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 16 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123PC141 | TM140123PT141 | TM140123PT141.MV | UHLE BOX PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 | TM1401ASD103 | TM140123PC141 | TM140123PV141 | TM140123PV141.OUT | UHLE BOX PRESSURE CV SETPOINT | PV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA202 |  | TM140123PI142 | TM140123PT142 | TM140123PT142.MV | PICK-UP BOX PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA202 |  | TM140123PC143 | TM140123PT143 | TM140123PT143.MV | SUCTION PRESS ROLL PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 | TM1401ASD103 | TM140123PC143 | TM140123PV143 | TM140123PV143.OUT | SUCTION PRESS ROLL PRESSURE CV SETPOINT | PV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123HS144 | TM140123SV144 | TM140123SV144 | VACUUM SHEAVE ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS144 | TM140123SV144.ZSC | TM140123SV144.GSC | VACUUM SHEAVE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS144 | TM140123SV144.ZSO | TM140123SV144.GSO | VACUUM SHEAVE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS144 | TM140123EV144 | TM140123EV144 | VACUUM SHEAVE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123HS145 | TM140123SV145 | TM140123SV145 | VACUUM SHEAVE ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS145 | TM140123SV145.ZSC | TM140123SV145.GSC | VACUUM SHEAVE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS145 | TM140123SV145.ZSO | TM140123SV145.GSO | VACUUM SHEAVE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS145 | TM140123EV145 | TM140123EV145 | VACUUM SHEAVE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123HS146 | TM140123SV146 | TM140123SV146 | VACUUM SHEAVE ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS146 | TM140123SV146.ZSC | TM140123SV146.GSC | VACUUM SHEAVE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS146 | TM140123SV146.ZSO | TM140123SV146.GSO | VACUUM SHEAVE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS146 | TM140123EV146 | TM140123EV146 | VACUUM SHEAVE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBA103 |  | TM140123LC147 | TM140123LT147 | TM140123LT147.MV | VACUUM SEPARATOR LEVEL | LT | DP Level Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3000 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 4 | Cutes
SHOWERS SYSTEM
P-OKITM07-10-320-07-PID-3004 | TM140121 |  |  | TM140121HS095 | TM140121SV095 | TM140121SV095 | WIRE CLEANING (FW2) SHOWER WATER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3004 | TM140121 | TM1401JBS205 |  | TM140121HS095 | TM140121SV095.ZSC | TM140121SV095.GSC | WIRE CLEANING (FW2) SHOWER WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3004 | TM140121 | TM1401JBS205 |  | TM140121HS095 | TM140121SV095.ZSO | TM140121SV095.GSO | WIRE CLEANING (FW2) SHOWER WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3004 | TM140121 | TM1401JBS205 |  | TM140121HS095 | TM140121EV095 | TM140121EV095 | WIRE CLEANING (FW2) SHOWER WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3004 | TM140121 |  |  | TM140121HS096 | TM140121SV096 | TM140121SV096 | SHEET SIDE FELT CLEANING(PW5) SHOWER WATER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3004 | TM140121 | TM1401JBS205 |  | TM140121HS096 | TM140121SV096.ZSC | TM140121SV096.GSC | SHEET SIDE FELT CLEANING(PW5) SHOWER WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3004 | TM140121 | TM1401JBS205 |  | TM140121HS096 | TM140121SV096.ZSO | TM140121SV096.GSO | SHEET SIDE FELT CLEANING(PW5) SHOWER WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3004 | TM140121 | TM1401JBS205 |  | TM140121HS096 | TM140121EV096 | TM140121EV096 | SHEET SIDE FELT CLEANING(PW5) SHOWER WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3004 | TM140121 |  |  | TM140121HS097 | TM140121SV097 | TM140121SV097 | FLOODED NIP (PW7) SHOWER WATER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 0
P-OKITM07-10-320-07-PID-3004 | TM140121 | TM1401JBS205 |  | TM140121HS097 | TM140121SV097.ZSC | TM140121SV097.GSC | FLOODED NIP (PW7) SHOWER WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3004 | TM140121 | TM1401JBS205 |  | TM140121HS097 | TM140121SV097.ZSO | TM140121SV097.GSO | FLOODED NIP (PW7) SHOWER WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3004 | TM140121 | TM1401JBS205 |  | TM140121HS097 | TM140121EV097 | TM140121EV097 | FLOODED NIP (PW7) SHOWER WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3004 | TM140121 |  |  | TM140121HS098 | TM140121SV098 | TM140121SV098 | TAIL CUTTER (PW3) SHOWER WATER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 0
P-OKITM07-10-320-07-PID-3004 | TM140121 | TM1401JBS205 |  | TM140121HS098 | TM140121SV098.ZSC | TM140121SV098.GSC | TAIL CUTTER (PW3) SHOWER WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3004 | TM140121 | TM1401JBS205 |  | TM140121HS098 | TM140121SV098.ZSO | TM140121SV098.GSO | TAIL CUTTER (PW3) SHOWER WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3004 | TM140121 | TM1401JBS205 |  | TM140121HS098 | TM140121EV098 | TM140121EV098 | TAIL CUTTER (PW3) SHOWER WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
FRESH WATER
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1401JBA102 |  | TM140122LC002 | TM140122LT002 | TM140122LT002.MV | WARM WATER TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3300 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1401JBA102 | TM1401ASD102 | TM140122LC002 | TM140122LV002 | TM140122LV002.OUT | WARM WATER TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3009 | TM140122 |  |  | TM140122TC004 | TM140122TE004 |  | WARM WATER TANK TEMPERATURE TEMPERATURE | TE | Temperature Sensor | Field
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1401JBA102 |  | TM140122TC004 | TM140122TT004 | TM140122TT004.MV | WARM WATER TANK TEMPERATURE TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [19 empty] | 1
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1401JBA102 | TM1401ASD102 | TM140122TC004 | TM140122TV004 | TM140122TV004.OUT | WARM WATER TANK TEMPERATURE TEMPERATURE CV SETPOINT | TV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1401JBA102 |  | TM140122PC008 | TM140122PT008 | TM140122PT008.MV | FELT HP SHOWER PUMP 1 OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 7 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1401JBA102 |  | TM140122PC009 | TM140122PT009 | TM140122PT009.MV | FELT HP SHOWER PUMP 2 OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 40 | Bar.g | [19 empty] | 1
COMPRESSED AIR
P-OKITM07-10-320-07-PID-3008 | TM140101 | TM1401JBA112 |  | TM140101PI002 | TM140101PT002 | TM140101PT002.MV | MILL COMPRESSED AIR PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3008 | TM140101 |  |  | TM140101HS003 | TM140101SV003 | TM140101SV003 | COMPRESSED AIR TO TM14.1 ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-3008 | TM140101 | TM1401JBS112 |  | TM140101HS003 | TM140101SV003.ZSC | TM140101SV003.GSC | COMPRESSED AIR TO TM14.1 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3008 | TM140101 | TM1401JBS112 |  | TM140101HS003 | TM140101SV003.ZSO | TM140101SV003.GSO | COMPRESSED AIR TO TM14.1 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3008 | TM140101 | TM1401JBS112 |  | TM140101HS003 | TM140101EV003 | TM140101EV003 | COMPRESSED AIR TO TM14.1 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3008 | TM140101 | TM1401JBA112 |  | TM140101PI004 | TM140101PT004 | TM140101PT004.MV | INSTRUMENT AIR STORAGE TANK #1 PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3008 | TM140101 |  |  | TM140101HS005 | TM140101SV005 | TM140101SV005 | INSTRUMENT AIR STORAGE TANK #1 DRAIN ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-3008 | TM140101 | TM1401JBS112 |  | TM140101HS005 | TM140101SV005.ZSC | TM140101SV005.GSC | INSTRUMENT AIR STORAGE TANK #1 DRAIN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3008 | TM140101 | TM1401JBS112 |  | TM140101HS005 | TM140101SV005.ZSO | TM140101SV005.GSO | INSTRUMENT AIR STORAGE TANK #1 DRAIN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3008 | TM140101 | TM1401JBS112 |  | TM140101HS005 | TM140101EV005 | TM140101EV005 | INSTRUMENT AIR STORAGE TANK #1 DRAIN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
NaOH SYSTEM
P-OKITM07-10-320-07-PID-3010 | TM140115 |  |  | TM140115HS013 | TM140115SV013 | TM140115SV013 | 32% NaOH TO TM14.1 ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3010 | TM140115 | TM1401JBS205 |  | TM140115HS013 | TM140115SV013.ZSC | TM140115SV013.GSC | 32% NaOH TO TM14.1 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3010 | TM140115 | TM1401JBS205 |  | TM140115HS013 | TM140115SV013.ZSO | TM140115SV013.GSO | 32% NaOH TO TM14.1 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3010 | TM140115 | TM1401JBS205 |  | TM140115HS013 | TM140115EV013 | TM140115EV013 | 32% NaOH TO TM14.1 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
YANKEE COATING
P-OKITM07-10-320-07-PID-3007 | TM140116 | Supplier JB |  | TM140116FC001 | TM140116FE001 |  | RELEASE AGENT PUMP 1 OUTLET FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3007 | TM140116 | Supplier JB |  | TM140116FC001 | TM140116FT001 | TM140116FT001.MV | RELEASE AGENT PUMP 1 OUTLET FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR |  |  | l / min | [19 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3007 | TM140116 | Supplier JB |  | TM140116FI003 | TM140116FE003 |  | RELEASE AGENT PUMP 2 OUTLET FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3007 | TM140116 | Supplier JB |  | TM140116FI003 | TM140116FT003 | TM140116FT003.MV | RELEASE AGENT PUMP 2 OUTLET FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR |  |  | l / min | [19 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3007 | TM140116 | Supplier JB |  | TM140116FI005 | TM140116FE005 |  | RELEASE AGENT PUMP 3 OUTLET FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3007 | TM140116 | Supplier JB |  | TM140116FI005 | TM140116FT005 | TM140116FT005.MV | RELEASE AGENT PUMP 3 OUTLET FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR |  |  | l / min | [19 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3007 | TM140116 | Supplier JB |  | TM140116PC007 | TM140116PT007 | TM140116PT007.MV | YANKEE COATING PUMP 1&2 OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 |  | Bar.g | [19 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3007 | TM140116 | Supplier JB |  | TM140116FI010 | TM140116FE010 |  | YANKEE COATING PUMP 1&2 OUTLET FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3007 | TM140116 | Supplier JB |  | TM140116FI010 | TM140116FT010 | TM140116FT010.MV | YANKEE COATING PUMP 1&2 OUTLET FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR |  |  | l / min | [19 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3007 | TM140116 | Supplier JB |  | TM140116LI021 | TM140116LI021 | TM140116LI021.MV | COATING TANK LEVEL | LI | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 |  | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 3 |  | HOLD,not finalised
P-OKITM07-10-320-07-PID-3007 | TM140116 | Supplier JB |  | TM140116LI022 | TM140116LI022 | TM140116LI022.MV | RELEASE TANK LEVEL | LI | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 |  | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 3 |  | HOLD,not finalised
P-OKITM07-10-320-07-PID-3007 | TM140116 | Supplier JB |  | TM140116LI023 | TM140116LI023 | TM140116LI023.MV | MAP TANK LEVEL | LI | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 |  | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 3 |  | HOLD,not finalised
STEAM AND CONDENSATE SYSTEM
P-OKITM07-10-320-07-PID-3006 | TM140135 |  |  | TM140135TI001 | TM140135TE001 |  | TO YANKEE 13.5 BAR STEAM TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 3 | PMP | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1401JBA112 |  | TM140135TI001 | TM140135TT001 | TM140135TT001.MV | TO YANKEE 13.5 BAR STEAM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 350 | ˚C | [19 empty] | 3 | PMP | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1401JBA112 |  | TM140135PI002 | TM140135PT002 | TM140135PT002.MV | TO YANKEE 13.5 BAR STEAM PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 15 | Bar.g | [19 empty] | 3 | PMP | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1401JBA112 |  | TM140135FI003 | TM140135FT003 | TM140135FT003.MV | TO YANKEE 13.5 BAR STEAM FLOW | FT | Vortex Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 11 | t/h | [19 empty] | 3 | PMP | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140135 |  |  | TM140135TI015 | TM140135TE015 |  | TO YANKEE 20 BAR STEAM TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 3 |  | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1401JBA112 |  | TM140135TI015 | TM140135TT015 | TM140135TT015.MV | TO YANKEE 20 BAR STEAM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 3 |  | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1401JBA112 |  | TM140135PI016 | TM140135PT016 | TM140135PT016.MV | TO YANKEE 20 BAR STEAM PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 25 | Bar.g | [19 empty] | 3 |  | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1401JBA112 |  | TM140135FI017 | TM140135FT017 | TM140135FT017.MV | TO YANKEE 20 BAR STEAM FLOW | FT | Vortex Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6.5 | t/h | [19 empty] | 3 |  | Already In PMP IO List
Hall ventilation
P-OKITM07-10-320-08-FLD-3001 | TM140100 | TM1401JBD202 |  | TM140100PDS102 | TM140100PDS102 | TM140100PDS102.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 1 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3001 | TM140100 | TM1401JBD202 |  | TM140100PDS103 | TM140100PDS103 | TM140100PDS103.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 1 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3001 | TM140100 | TM1401JBD301 |  | TM140100PDS104 | TM140100PDS104 | TM140100PDS104.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 1 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3001 | TM140100 | TM1401JBD301 |  | TM140100PDS105 | TM140100PDS105 | TM140100PDS105.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 1 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3001 | TM140100 | TM1401JBD301 |  | TM140100PDS106 | TM140100PDS106 | TM140100PDS106.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 1 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3001 | TM140100 | TM1401JBD301 |  | TM140100XS107 | TM140100XS107 | TM140100XS107 | TM 14.1 EXHAUST AIR FAN1 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3001 | TM140100 | TM1401JBD301 |  | TM140100XS108 | TM140100XS108 | TM140100XS108 | TM 14.1 EXHAUST AIR FAN2 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3001 | TM140100 | TM1401JBD301 |  | TM140100XS109 | TM140100XS109 | TM140100XS109 | TM 14.1 EXHAUST AIR FAN3 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3001 | TM140100 | TM1401JBD301 |  | TM140100XS110 | TM140100XS110 | TM140100XS110 | TM 14.1 EXHAUST AIR FAN4 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3001 | TM140100 | TM1401JBD301 |  | TM140100XS111 | TM140100XS111 | TM140100XS111 | TM 14.1 EXHAUST AIR FAN5 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3001 | TM140100 | TM1401JBD301 |  | TM140100XS112 | TM140100XS112 | TM140100XS112 | TM 14.1 EXHAUST AIR FAN6 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 | HVAC Vendor
HVAC Air Condition
P-OKITM07-10-320-08-FLD-3000 | TM140100 | NA |  | TM140100PDS001 | TM140100PDS001 | TM140100PDS001.L | TM 14.1 TM MCC ROOM AIR FAN FILTER 1 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3000 | TM140100 | NA |  | TM140100PDS002 | TM140100PDS002 | TM140100PDS002.L | TM 14.1 TM MCC ROOM AIR FAN FILTER 2 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3000 | TM140100 | NA |  | TM140100PDS003 | TM140100PDS003 | TM140100PDS003.L | TM 14.1 TM MCC ROOM AIR FAN FILTER 3 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3000 | TM140100 | NA |  | TM140100PDS004 | TM140100PDS004 | TM140100PDS004.L | TM 14.1 TM MCC ROOM AIR FAN FILTER 4 DIFFERENTIAL PRESSURE(MAU1) | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3000 | TM140100 | NA |  | TM140100PDS005 | TM140100PDS005 | TM140100PDS005.L | TM 14.1 TM MCC ROOM AIR FAN FILTER 4 DIFFERENTIAL PRESSURE(MAU2) | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3000 | TM140100 | NA |  | TM140100XS006 | TM140100XS006 | TM140100XS006 | TM 14.1 TM MCC ROOM AC1 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3000 | TM140100 | NA |  | TM140100XS007 | TM140100XS007 | TM140100XS007 | TM 14.1 TM MCC ROOM AC2 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3000 | TM140100 | NA |  | TM140100XS008 | TM140100XS008 | TM140100XS008 | TM 14.1 TM MCC ROOM AC3 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3000 | TM140100 | NA |  | TM140100XS009 | TM140100XS009 | TM140100XS009 | TM 14.1 TM MCC ROOM AC4 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3000 | TM140100 | NA |  | TM140100II010 | TM140100IT010 | TM140100IT010.MV | TM 14.1 TM MCC ROOM AC PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | [22 empty] | 3 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3000 | TM140100 | NA |  | TM140100II011 | TM140100IT011 | TM140100IT011.MV | TM 14.1 SUPPLY FAN PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | [22 empty] | 3 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3000 | TM140100 | NA |  | TM140100II012 | TM140100IT012 | TM140100IT012.MV | TM 14.1 EXHAUST FAN PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | [22 empty] | 3 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3000 | TM140100 | NA |  | TM140100TI013 | TM140100TT013 | TM140100TT013.MV | TM 14.1 TM MCC ROOM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 0 | 50 | ˚C | [19 empty] | 3 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3000 | TM140100 | NA |  | TM140100MI014 | TM140100MT014 | TM140100MT014.MV | TM 14.1 TM MCC ROOM HUMIDITY | MT | Humidity Transmitter(Integrated In TT) | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 40 | 60 | % | [19 empty] | 3 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3000 | TM140100 | NA |  | TM140100TI015 | TM140100TT015 | TM140100TT015.MV | TM 14.1 TM RACK ROOM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 0 | 50 | ˚C | [19 empty] | 3 | HVAC Vendor
P-OKITM07-10-320-08-FLD-3000 | TM140100 | NA |  | TM140100MI016 | TM140100MT016 | TM140100MT016.MV | TM 14.1 TM RACK ROOM HUMIDITY | MT | Humidity Transmitter(Integrated In TT) | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 40 | 60 | % | [19 empty] | 3 | HVAC Vendor

## 14.1 exchange communication lst
PMT: |  |  |  |  | Design Institute: |  |  | Project No. | P-OKITM07-10 | [6 empty] | EXCHANGE COMMUNICTION LIST
[8 empty] | Project Name | DETAIL ENGINEERING FOR 4(FOUR) UNITS TISSUE MACHINE
[8 empty] | Doc. No. | P-OKITM07-10-320-06-LST-3005 | [7 empty] | Abbreviations
Owner: | [7 empty] | Rev. No. | 4 |  |  | Prep'd by | Dengzuijie |  |  |  | EER Electronic Equipment Room |  |  |  | SQRT Square Root
[8 empty] | Purpose | Final |  |  | Chk'd by | Chengjianguo |  |  |  | CCR Control Center Room
[8 empty] | Date | 8,30,2021 |  |  | Appv'd by | LiXiangdong |  |  |  | ESP Electrostatic Precipitator
P&ID No. | Area | Motor Tag reference | Loop No. | Tag No. | System Tag No. | Service Description | Signal Tag | Instrument Type | Location | System | IO Type | Signal |  |  | IO Loc. | PV LO | PV HI | Eng. Unit | Alarm | [6 empty] | State "0" | State "1" | CV Fail Action | CV Ctrl Action | PV CHAR | From |  | Cable |  |  | To |  | Rev. | Supply | Remarks
[12 empty] | Type | Power | Wire |  |  |  |  | LLL | LL | L | Nor. | H | HH | HHH | [5 empty] | JB/Panel No. | TB | Cable Number | Cable Type | Cable Order | Cabinet No. | TB |  | By
MACHINE BROKE
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM140117U003 | TM140117SC025 | TM140117SX025 | TM140117SX025.PRO | BROKE INTERIM TOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM140117U001 | TM140117SC050 | TM140117SX050 | TM140117SX050.PRO | BROKE DEFLAKED CHEST PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM140117A004 | TM140117SC054 | TM140117SX054 | TM140117SX054.PRO | YANKEE PULPER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC |  | MCC | [20 empty] | 2
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM140117U002 | TM140117SC092 | TM140117SX092 | TM140117SX092.PRO | BROKE THICKENER TANK PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
STOCK APPROACH
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120U001 | TM140120SC013 | TM140120SX013 | TM140120SX013.PRO | MIXING CHEST PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120M001 | TM140120EC033 | TM140120SX013 | TM140120SX013.PRO | TICKLER REFINER POWER VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120U003 | TM140120SC046 | TM140120SX046 | TM140120SX046.PRO | SWEETENER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120U004 | TM140120SC056 | TM140120SX056 | TM140120SX056.PRO | MACHINE CHEST PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120U006 | TM140120SC071 | TM140120SX071 | TM140120SX071.PRO | FAN PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3001 | TM140120 | TM140120U007 | TM140120SC102 | TM140120SX102 | TM140120SX102.PRO | W.W OVERFLOW CHEST PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3001 | TM140115 |  | TM140115FC005 | TM140115FX005A | TM140115FX005A.PRO | WET STRENGHT AGENT TO MIXING CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3001 | TM140115 |  | TM140115FC005 | TM140115FX005B | TM140115FX005B.PRO | WET STRENGHT AGENT TO MIXING CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3001 | TM140115 |  | TM140115FC006 | TM140115FX006A | TM140115FX006A.PRO | DRY STRENGHT AGENT TO MACHINE CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3001 | TM140115 |  | TM140115FC006 | TM140115FX006B | TM140115FX006B.PRO | DRY STRENGHT AGENT TO MACHINE CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3001 | TM140115 |  | TM140115FC007 | TM140115FX007A | TM140115FX007A.PRO | SOFT AGENT TO MIXING CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3001 | TM140115 |  | TM140115FC007 | TM140115FX007B | TM140115FX007B.PRO | SOFT AGENT TO MIXING CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3001 | TM140115 |  | TM140115FC008 | TM140115FX008A | TM140115FX008A.PRO | CMC TO FAN PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3001 | TM140115 |  | TM140115FC008 | TM140115FX008B | TM140115FX008B.PRO | CMC TO FAN PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
WHITE WATER AND FIBRE RECOVERY
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121M001 | TM140121SC027 | TM140121SX027 | TM140121SX027.PRO | DISC FILTER MOTOR SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121U001 | TM140121SC029 | TM140121SX029 | TM140121SX029.PRO | DISC FILTER FEED PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121U002 | TM140121SC030 | TM140121SX030 | TM140121SX030.PRO | TM AREA CRC PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121U003 | TM140121SC031 | TM140121SX031 | TM140121SX031.PRO | YANKEE-TRIM PULPER & OVER FLOW PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121U007 | TM140121SC032 | TM140121SX032 | TM140121SX032.PRO | CLARIFIED TANK PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121U008 | TM140121SC033 | TM140121SX033 | TM140121SX033.PRO | DISC FILTER SHOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121U004 | TM140121SC047 | TM140121SX047 | TM140121SX047.PRO | REC PULP CHEST PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121U009 | TM140121SC048 | TM140121SX048 | TM140121SX048.PRO | CWW LP SHOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121U006 | TM140121SC049 | TM140121SX049 | TM140121SX049.PRO | CWW HP SHOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121U005 | TM140121SC051 | TM140121SX051 | TM140121SX051.PRO | CLOUDY CIRCULATION PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121U011 | TM140121SC052 | TM140121SX052 | TM140121SX052.PRO | SCWW LP SHOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121U013 | TM140121SC142 | TM140121SX142 | TM140121SX142.PRO | SCWW HP SHOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121U012 | TM140121SC143 | TM140121SX143 | TM140121SX143.PRO | PMP DEMAND & CLEANING PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3005 | TM140121 | TM140121U014 | TM140121SC146 | TM140121SX146 | TM140121SX146.PRO | DUST SCWW PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
FRESH WATER
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM140122U008 | TM140122SC031 | TM140122SX031 | TM140122SX031.PRO | WARM WATER PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM140122U009 | TM140122SC032 | TM140122SX032 | TM140122SX032.PRO | WARM WATER PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM140122U010 | TM140122SC033 | TM140122SX033 | TM140122SX033.PRO | FELT HP SHOWER PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM140122U011 | TM140122SC034 | TM140122SX034 | TM140122SX034.PRO | FELT HP SHOWER PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
YANKEE COATING
P-OKITM07-10-320-07-PID-3007 | TM140116 |  | TM140116SC002 | TM140116SX002 | TM140116SX002.PRO | RELEASE AGENT PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3007 | TM140116 |  | TM140116SC004 | TM140116SX004 | TM140116SX004.PRO | RELEASE AGENT PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3007 | TM140116 |  | TM140116SC006 | TM140116SX006 | TM140116SX006.PRO | RELEASE AGENT PUMP 3 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3007 | TM140116 |  | TM140116SC008 | TM140116SX008 | TM140116SX008.PRO | YANKEE COATING PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3007 | TM140116 |  | TM140116SC009 | TM140116SX009 | TM140116SX009.PRO | YANKEE COATING PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B

## IO Summary
I/O COUNT SUMMARY
| AI | AO | DI | DO | TOTAL | REMARK
DCS | 118 | 45 | 195 | 78 | 436
SIS | 0 | 0 | 0 | 0 | 0
SUM | 118 | 45 | 195 | 78 | 436

## Definitions
P&ID No. | The P&ID drawing number where the equipment is located.
Area | The Area where the equipment is located
Loop No. | Loop Number
Tag No. | Tag Name according to APP guideline
System Tag No. | Tag name to be appeared in DCS
Service Description | Process/service description
Signal Tag | Signal Tagname
Instrument Type | Type of instrument
Location | Location of the instrument
System | in DCS, PLC or local
IO Type | Type of input or output
Signal - Type | Signal type
Signal - Power | Power for the signal
Signal - Wire | wiring configuration
IO Loc. | Input and Output location
PV LO | Range Low
PV HI | Range High
Eng. Unit | Engineering Unit
Alarm | LLL- Low Low Low, HHH- High High High etc
State "0" | For Valves, If signal is zero, what willl be the valve opening.
State "1" | For Valves, If signal is one, what willl be the valve opening.
CV fail Action | For Valves, If air fails, what willl be the valve status.
CV Control Action | For Valves, Direction of the control.
PV CHAR | Process value characteristics
Rev | Revision
Supply By | Supplier name
Remarks