## Common Area
PMT: | [5 empty] | Design Institute: |  |  | Project No. | P-OKITM07-10 | [6 empty] | DCS I/O Database
[9 empty] | Project Name | DETAIL ENGINEERING FOR 4(FOUR) UNITS TISSUE MACHINE
[9 empty] | Doc. No. | P-OKITM07-10-320-06-LST-3015 | [7 empty] | Abbreviations
Owner: | [8 empty] | Rev. No. | 4 |  |  | Prep'd by | Dengzuijie |  |  |  | EER Electronic Equipment Room |  |  |  | SQRT Square Root
[9 empty] | Purpose | Final |  |  | Chk'd by | Chengjianguo |  |  |  | CCR Control Center Room
[9 empty] | Date | 30,8,2021 |  |  | Appv'd by | LiXiangdong |  |  |  | ESP Electrostatic Precipitator
P&ID No. | Area | JB No. | ASD No. | Loop No. | Tag No. | System Tag No. | Service Description | Signal Tag | Instrument Type | Location | System | IO Type | Signal |  |  | IO Loc. | PV LO | PV HI | Eng. Unit | Alarm | [6 empty] | State "0" | State "1" | CV Fail Action | CV Ctrl Action | PV CHAR | From |  | Cable |  |  | To |  | Rev. | Supply | Remarks
[13 empty] | Type | Power | Wire |  |  |  |  | LLL | LL | L | Nor. | H | HH | HHH | [5 empty] | JB/Panel No. | TB | Cable Number | Cable Type | Cable Order | Cabinet No. | TB |  | By
MACHINE BROKE
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1401JBD112 |  | TM140117FS004 | TM140117FS004 | TM140117FS004.L | SEALING WATER TO BROKE INTERIM TOWER PUMP 1 FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1402JBA112 | TM1402ASD113 | TM140117HC-018 | TM140117HV-018 | TM140117HV-018.OUT | BROKE INTERIM TOWER PUMP 2 INLET DILUTION WATER CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | CCC | 0 | 100 | % | [19 empty] | 1 |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3002 | TM140117 |  |  | TM140117FI019 | TM140117FE019 |  | BROKE INTERIM TOWER PUMP 2 OUTLET TO SP2 PULPER FLOW | FE | Magnetic flow Sensor | Field | [30 empty] | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3002 | TM140117 | TM1402JBA112 |  | TM140117FI019 | TM140117FT019 | TM140117FT019.MV | BROKE INTERIM TOWER PUMP 2 OUTLET TO SP2 PULPER FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 3500 | l / min | [19 empty] | 1 |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD112 |  | TM140317FS004 | TM140317FS004 | TM140317FS004.L | SEALING WATER TO BROKE INTERIM TOWER PUMP 1 FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA112 |  | TM140317HC-018 | TM140317HV-018 | TM140317HV-018.OUT | BROKE INTERIM TOWER PUMP 2 INLET DILUTION WATER CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | CCC | 0 | 100 | % | [19 empty] | 1 |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317FI019 | TM140317FE019 |  | BROKE INTERIM TOWER PUMP 2 OUTLET TO SP2 PULPER FLOW | FE | Magnetic flow Sensor | Field | [30 empty] | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA112 |  | TM140317FI019 | TM140317FT019 | TM140317FT019.MV | BROKE INTERIM TOWER PUMP 2 OUTLET TO SP2 PULPER FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 3500 | l / min | [19 empty] | 1 |  | Common for TM14.3&4
FRESH WATER
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1401JBA111 |  | TM140122LC001 | TM140122LT001 | TM140122LT001.MV | FRESH WATER TANK 1 LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 4200 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1 |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1401JBA111 | TM1401ASD112 | TM140122LC001 | TM140122LV001 | TM140122LV001.OUT | FRESH WATER TANK 1 LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3009 | TM140122 |  |  | TM140122FI003 | TM140122FE003 |  | FRESH WATER TO TM14.1 & TM14.2 FLOW | FE | Magnetic Flow Sensor | Field | DCS | [27 empty] | C |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1401JBA111 |  | TM140122FI003 | TM140122FT003 | TM140122FT003.MV | FRESH WATER TO TM14.1 & TM14.2 FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 6600 | l/min | [19 empty] | 1 |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3009 | TM140122 |  |  | TM140122HS005 | TM140122SV005 | TM140122SV005 | COOLING TOWER 1 RETURN WATER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | C |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1405JBS003 |  | TM140122HS005 | TM140122SV005.ZSC | TM140122SV005.GSC | COOLING TOWER 1 RETURN WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1405JBS003 |  | TM140122HS005 | TM140122SV005.ZSO | TM140122SV005.GSO | COOLING TOWER 1 RETURN WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1405JBS003 |  | TM140122HS005 | TM140122EV005 | TM140122EV005 | COOLING TOWER 1 RETURN WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3009 | TM140122 |  |  | TM140122HS006 | TM140122SV006 | TM140122SV006 | COOLING TOWER 2 RETURN WATER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | C |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1405JBS003 |  | TM140122HS006 | TM140122SV006.ZSC | TM140122SV006.GSC | COOLING TOWER 2 RETURN WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1405JBS003 |  | TM140122HS006 | TM140122SV006.ZSO | TM140122SV006.GSO | COOLING TOWER 2 RETURN WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1405JBS003 |  | TM140122HS006 | TM140122EV006 | TM140122EV006 | COOLING TOWER 2 RETURN WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1405JBS003 |  | TM140122XISA007 | TM140122XS007 | TM140122XS007.HH | COOLING TOWER 1 PUMP 1 VIBRATION HIGH | XS | Vibration Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1405JBS003 |  | TM140122XISA008 | TM140122XS008 | TM140122XS008.HH | COOLING TOWER 1 PUMP 1 VIBRATION HIGH | XS | Vibration Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1401JBA111 |  | TM140122PI011 | TM140122PT011 | TM140122PT011.MV | FRESH WATER FILTER INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1401JBA111 |  | TM140122PI012 | TM140122PT012 | TM140122PT012.MV | FRESH WATER FILTER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3009 | TM140122 |  |  | TM140122PDI013 | TM140122PDX013 | TM140122PDX013.SOF | FRESH WATER FILTER DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function | [25 empty] | C |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1401JBA111 |  | TM140122PI014 | TM140122PT014 | TM140122PT014.MV | SEALING WATER FILTER INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1 |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1401JBA111 |  | TM140122PI015 | TM140122PT015 | TM140122PT015.MV | SEALING WATER FILTER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1 |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3009 | TM140122 |  |  | TM140122PDI016 | TM140122PDX016 | TM140122PDX016.SOF | SEALING WATER FILTER DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function | [25 empty] | C |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1401JBA111 |  | TM140122PI017 | TM140122PT017 | TM140122PT017.MV | HP SEALING WATER PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 16 | Bar.g | [19 empty] | 1 |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM140122CP01 |  | TM140122XS018 | TM140122S1.018 | TM140122S1.018 | FRESH WATER FILTER LOCAL PANEL | S1 | Differential Pressure High alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM140122CP01 |  | TM140122XS018 | TM140122S2.018 | TM140122S2.018 | FRESH WATER FILTER LOCAL PANEL | S2 | Flush alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM140122CP01 |  | TM140122XS018 | TM140122S3.018 | TM140122S3.018 | FRESH WATER FILTER LOCAL PANEL | S3 | Power Failure alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM140122CP02 |  | TM140122XS019 | TM140122S1.019 | TM140122S1.019 | SEALING WATER FILTER LOCAL PANEL | S1 | Differential Pressure High alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM140122CP02 |  | TM140122XS019 | TM140122S2.019 | TM140122S2.019 | SEALING WATER FILTER LOCAL PANEL | S2 | Flush alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM140122CP02 |  | TM140122XS019 | TM140122S3.019 | TM140122S3.019 | SEALING WATER FILTER LOCAL PANEL | S3 | Power Failure alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1403JBA103 |  | TM140122PI021 | TM140122PT021 | TM140122PT021.MV | COOLING WATER FILTER INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1403JBA103 |  | TM140122PI022 | TM140122PT022 | TM140122PT022.MV | COOLING WATER FILTER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3009 | TM140122 |  |  | TM140122PDI023 | TM140122PDX023 | TM140122PDX023.SOF | COOLING WATER FILTER DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function | [25 empty] | C |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3009 | TM140122 |  |  | TM140122TI024 | TM140122TE024 |  | COOLING WATER PUMP 1&2&3 INLET TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | C |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM1403JBA103 |  | TM140122TI024 | TM140122TT024 | TM140122TT024.MV | COOLING WATER PUMP 1&2&3 INLET TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [19 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM140122CP03 |  | TM140122XS025 | TM140122S1.025 | TM140122S1.025 | COOLING WATER FILTER LOCAL PANEL | S1 | Differential Pressure High alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM140122CP03 |  | TM140122XS025 | TM140122S2.025 | TM140122S2.025 | COOLING WATER FILTER LOCAL PANEL | S2 | Flush alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM140122CP03 |  | TM140122XS025 | TM140122S3.025 | TM140122S3.025 | COOLING WATER FILTER LOCAL PANEL | S3 | Power Failure alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM1404JBA111 |  | TM140322LC001 | TM140322LT001 | TM140322LT001.MV | FRESH WATER TANK 1 LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 4200 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1 |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM1404JBA111 | TM1403ASD112 | TM140322LC001 | TM140322LV001 | TM140322LV001.OUT | FRESH WATER TANK 1 LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3709 | TM140322 |  |  | TM140322FI003 | TM140322FE003 |  | FRESH WATER TO TM14.1 & TM14.2 FLOW | FE | Magnetic Flow Sensor | Field | DCS | [27 empty] | C |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM1404JBA111 |  | TM140322FI003 | TM140322FT003 | TM140322FT003.MV | FRESH WATER TO TM14.1 & TM14.2 FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 6600 | l/min | [19 empty] | 1 |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM1404JBA111 |  | TM140322PI011 | TM140322PT011 | TM140322PT011.MV | FRESH WATER FILTER INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM1404JBA111 |  | TM140322PI012 | TM140322PT012 | TM140322PT012.MV | FRESH WATER FILTER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3709 | TM140322 |  |  | TM140322PDI013 | TM140322PDX013 | TM140322PDX013.SOF | FRESH WATER FILTER DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function | [25 empty] | C |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM1404JBA111 |  | TM140322PI014 | TM140322PT014 | TM140322PT014.MV | SEALING WATER FILTER INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1 |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM1404JBA111 |  | TM140322PI015 | TM140322PT015 | TM140322PT015.MV | SEALING WATER FILTER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1 |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3709 | TM140322 |  |  | TM140322PDI016 | TM140322PDX016 | TM140322PDX016.SOF | SEALING WATER FILTER DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function | [25 empty] | C |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM1404JBA111 |  | TM140322PI017 | TM140322PT017 | TM140322PT017.MV | HP SEALING WATER PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 16 | Bar.g | [19 empty] | 1 |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM140322CP01 |  | TM140322XS018 | TM140322S1.018 | TM140322S1.018 | FRESH WATER FILTER LOCAL PANEL | S1 | Differential Pressure High alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM140322CP01 |  | TM140322XS018 | TM140322S2.018 | TM140322S2.018 | FRESH WATER FILTER LOCAL PANEL | S2 | Flush alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM140322CP01 |  | TM140322XS018 | TM140322S3.018 | TM140322S3.018 | FRESH WATER FILTER LOCAL PANEL | S3 | Power Failure alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM140322CP02 |  | TM140322XS019 | TM140322S1.019 | TM140322S1.019 | SEALING WATER FILTER LOCAL PANEL | S1 | Differential Pressure High alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM140322CP02 |  | TM140322XS019 | TM140322S2.019 | TM140322S2.019 | SEALING WATER FILTER LOCAL PANEL | S2 | Flush alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM140322CP02 |  | TM140322XS019 | TM140322S3.019 | TM140322S3.019 | SEALING WATER FILTER LOCAL PANEL | S3 | Power Failure alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
NaOH SYSTEM
P-OKITM07-10-320-07-PID-3010 | TM140115 | TM1402JBA201 |  | TM140115LI009 | TM140115LT009 | TM140115LT009.MV | NaOH STORAGE TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 1500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1 |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3010 | TM140115 |  |  | TM140115FI010 | TM140115FE010 |  | 10% NaOH TO NaOH STORAGE TANK FLOW | FE | Magnetic Flow Sensor | Field | DCS | [27 empty] | C |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3010 | TM140115 | TM1402JBA201 |  | TM140115FI010 | TM140115FT010 | TM140115FT010.MV | 10% NaOH TO NaOH STORAGE TANK FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 240 | l/min | [19 empty] | 1 |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3010 | TM140115 |  |  | TM140115HS011 | TM140115SV011 | TM140115SV011 | 10% NaOH TO STORAGE TANK ON/OFF VALVE | SV | On/Off Valve | [29 empty] | C |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3010 | TM140115 | TM1402JBS202 |  | TM140115HS011 | TM140115SV011.ZSC | TM140115SV011.GSC | 10% NaOH TO STORAGE TANK ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3010 | TM140115 | TM1402JBS202 |  | TM140115HS011 | TM140115SV011.ZSO | TM140115SV011.GSO | 10% NaOH TO STORAGE TANK ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3010 | TM140115 | TM1402JBS202 |  | TM140115HS011 | TM140115EV011 | TM140115EV011 | 10% NaOH TO STORAGE TANK ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3010 | TM140115 |  |  | TM140115FI012 | TM140115FE012 |  | 32% NaOH TO TM14.1&14.2 FLOW | FE | Magnetic Flow Sensor | Field | DCS | [27 empty] | C |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3010 | TM140115 | TM1401JBA111 |  | TM140115FI012 | TM140115FT012 | TM140115FT012.MV | 32% NaOH TO TM14.1&14.2 FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 240 | l/min | [19 empty] | 1 |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3710 | TM140315 | TM1404JBA201 |  | TM140315LI009 | TM140315LT009 | TM140315LT009.MV | NaOH STORAGE TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 1500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1 |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3710 | TM140315 |  |  | TM140315FI010 | TM140315FE010 |  | 10% NaOH TO NaOH STORAGE TANK FLOW | FE | Magnetic Flow Sensor | Field | DCS | [27 empty] | C |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3710 | TM140315 | TM1404JBA201 |  | TM140315FI010 | TM140315FT010 | TM140315FT010.MV | 10% NaOH TO NaOH STORAGE TANK FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 240 | l/min | [19 empty] | 1 |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3710 | TM140315 |  |  | TM140315HS011 | TM140315SV011 | TM140315SV011 | 10% NaOH TO STORAGE TANK ON/OFF VALVE | SV | On/Off Valve | [29 empty] | C |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3710 | TM140315 | TM1404JBS202 |  | TM140315HS011 | TM140315SV011.ZSC | TM140315SV011.GSC | 10% NaOH TO STORAGE TANK ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3710 | TM140315 | TM1404JBS202 |  | TM140315HS011 | TM140315SV011.ZSO | TM140315SV011.GSO | 10% NaOH TO STORAGE TANK ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3710 | TM140315 | TM1404JBS202 |  | TM140315HS011 | TM140315EV011 | TM140315EV011 | 10% NaOH TO STORAGE TANK ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3710 | TM140315 |  |  | TM140315FI012 | TM140315FE012 |  | 32% NaOH TO TM14.3&14.4 FLOW | FE | Magnetic Flow Sensor | Field | DCS | [27 empty] | C |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3710 | TM140315 | TM1404JBA111 |  | TM140315FI012 | TM140315FT012 | TM140315FT012.MV | 32% NaOH TO TM14.3&14.4 FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 240 | l/min | [19 empty] | 1 |  | Common for TM14.3&4
STEAM AND CONDENSATE SYSTEM
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1400JBA005 |  | TM140135PI021 | TM140135PT021 | TM140135PT021.MV | 35 BAR STEAM BEFORE PRDS PRESSURE | PT | Pressure Transmitter | Field | PRDS PLC | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 40 | Bar.g | [19 empty] | 1 | PRDS Supplier | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1400JBA005 |  | TM140135PC022 | TM140135PT022 | TM140135PT022.MV | AFTER PRDS PRESSURE | PT | Pressure Transmitter | Field | PRDS PLC | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 25 | Bar.g | [19 empty] | 1 | PRDS Supplier | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1400JBA005 | TM1400ASD006 | TM140135PC022 | TM140135PV022 | TM140135PV022.OUT | AFTER PRDS PRESSURE CV SETPOINT | PV | Control Valve | Field | PRDS PLC | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 | PRDS Supplier | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 |  |  | TM140135TC023 | TM140135TE023 |  | AFTER PRDS TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 0 | PRDS Supplier | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1400JBA005 |  | TM140135TC023 | TM140135TT023 | TM140135TT023.MV | AFTER PRDS TEMPERATURE | TT | Temperature Transmitter | Field | PRDS PLC | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 1 | PRDS Supplier | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1400JBA005 | TM1400ASD006 | TM140135TC023 | TM140135TV023 | TM140135TV023.OUT | AFTER PRDS TEMPERATURE CV SETPOINT | TV | Control Valve | Field | PRDS PLC | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 | PRDS Supplier | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 |  |  | TM140135TI029 | TM140135TE029 |  | 35 BAR STEAM BEFORE PRDS TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 0 | PRDS Supplier | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1400JBA005 |  | TM140135TI029 | TM140135TT029 | TM140135TT029.MV | 35 BAR STEAM BEFORE PRDS TEMPERATURE | TT | Temperature Transmitter | Field | PRDS PLC | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 1 | PRDS Supplier | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1400JBA004 |  | TM140135PC030 | TM140135PC030 | TM140135PC030.MV | PRDS WATER PUMP OUTLET PRESSURE | PC | Pressure Transmitter | Field | PRDS PLC | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 40 | Bar.g | [19 empty] | 3 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1400JBA004 | TM1400ASD005 | TM140135PC030 | TM140135PV030 | TM140135PV030.OUT | PRDS WATER PUMP OUTLET PRESSURE CV SETPOINT | PV | Control Valve | Field | PRDS PLC | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 3 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1402JBA112 |  | TM140135LC031 | TM140135LT031 | TM140135LT031.MV | CONDENSATE TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 4500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1401JBD112 |  | TM140135FS032 | TM140135FS032 | TM140135FS032.L | CONDENSATE TANK PUMP 1 FLOW | FS | Flow Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1401JBD112 |  | TM140135FS033 | TM140135FS033 | TM140135FS033.L | CONDENSATE TANK PUMP SPARE FLOW | FS | Flow Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 |  |  | TM140135HS034 | TM140135SV034 | TM140135SV034 | CONDENSATE TANK PUMP TO RAW POLISHER STORAGE ON/OFF VALVE | SV | On/Off Valve | [29 empty] | C |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1402JBS113 |  | TM140135HS034 | TM140135SV034.ZSC | TM140135SV034.GSC | CONDENSATE TANK PUMP TO RAW POLISHER STORAGE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1402JBS113 |  | TM140135HS034 | TM140135SV034.ZSO | TM140135SV034.GSO | CONDENSATE TANK PUMP TO RAW POLISHER STORAGE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1402JBS113 |  | TM140135HS034 | TM140135EV034 | TM140135EV034 | CONDENSATE TANK PUMP TO RAW POLISHER STORAGE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 |  |  | TM140135HS035 | TM140135SV035 | TM140135SV035 | CONDENSATE TANK PUMP DRAINAGE ON/OFF VALVE | SV | On/Off Valve | [29 empty] | C |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1402JBS113 |  | TM140135HS035 | TM140135SV035.ZSC | TM140135SV035.GSC | CONDENSATE TANK PUMP DRAINAGE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1402JBS113 |  | TM140135HS035 | TM140135SV035.ZSO | TM140135SV035.GSO | CONDENSATE TANK PUMP DRAINAGE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1402JBS113 |  | TM140135HS035 | TM140135EV035 | TM140135EV035 | CONDENSATE TANK PUMP DRAINAGE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 |  |  | TM140135AC036 | TM140135AE036 |  | CONDENSATE TANK PUMP TO RAW POLISHER STORAGE CONDUCTIVITY | AE | Conductivity Sensor | Field | DCS | [27 empty] | C |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1402JBA112 |  | TM140135AC036 | TM140135AT036 | TM140135AT036.MV | CONDENSATE TANK PUMP TO RAW POLISHER STORAGE CONDUCTIVITY | AT | Conductivity Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | xx | us/mm | [19 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1400JBA004 |  | TM140135FI037 | TM140135FT037 | TM140135FT037.MV | CONDENSATE TANK PUMP TO RAW POLISHER STORAGE FLOW | FT | Vortex Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 1600 | l/min | [19 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 |  |  | TM140135HS040 | TM140135SV040 | TM140135SV040 | CONDENSATE TANK PUMP TO SP1 CONDENSATE BUFFER TANK ON/OFF VALVE | SV | On/Off Valve | [29 empty] | C |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1400JBS011 |  | TM140135HS040 | TM140135SV040.ZSC | TM140135SV040.GSC | CONDENSATE TANK PUMP TO SP1 CONDENSATE BUFFER TANK ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1400JBS011 |  | TM140135HS040 | TM140135SV040.ZSO | TM140135SV040.GSO | CONDENSATE TANK PUMP TO SP1 CONDENSATE BUFFER TANK ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM1400JBS011 |  | TM140135HS040 | TM140135EV040 | TM140135EV040 | CONDENSATE TANK PUMP TO SP1 CONDENSATE BUFFER TANK ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140335 | TM1403JBA112 |  | TM140335LC031 | TM140335LT031 | TM140335LT031.MV | CONDENSATE TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 4500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1 |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3006 | TM140335 | TM1403JBD112 |  | TM140335FS032 | TM140335FS032 | TM140335FS032.L | CONDENSATE TANK PUMP 1 FLOW | FS | Flow Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3006 | TM140335 | TM1403JBD112 |  | TM140335FS033 | TM140335FS033 | TM140335FS033.L | CONDENSATE TANK PUMP SPARE FLOW | FS | Flow Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  | Common for TM14.3&4
VACUUM SYSTEM
P-OKITM07-10-320-07-PID-3003 | TM140123 |  |  | TM140123HS102 | TM140123SV102 | TM140123SV102 | VACUUM SHEAVE ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4 |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS102 | TM140123SV102.ZSC | TM140123SV102.GSC | VACUUM SHEAVE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4 |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS102 | TM140123SV102.ZSO | TM140123SV102.GSO | VACUUM SHEAVE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4 |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3003 | TM140123 | TM1401JBS102 |  | TM140123HS102 | TM140123EV102 | TM140123EV102 | VACUUM SHEAVE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4 |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323HS102 | TM140323SV102 | TM140323SV102 | VACUUM SHEAVE ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4 |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS102 | TM140323SV102.ZSC | TM140323SV102.GSC | VACUUM SHEAVE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4 |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS102 | TM140323SV102.ZSO | TM140323SV102.GSO | VACUUM SHEAVE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4 |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS102 | TM140323EV102 | TM140323EV102 | VACUUM SHEAVE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4 |  | Common for TM14.3&4

## Exchange Communication list
PMT: |  |  |  |  | Design Institute: |  |  | Project No. | P-OKITM07-10 | [6 empty] | EXCHANGE COMMUNICTION LIST
[8 empty] | Project Name | DETAIL ENGINEERING FOR 4(FOUR) UNITS TISSUE MACHINE
[8 empty] | Doc. No. | P-OKITM07-10-320-06-LST-3015 | [7 empty] | Abbreviations
Owner: | [7 empty] | Rev. No. | 4 |  |  | Prep'd by | Dengzuijie |  |  |  | EER Electronic Equipment Room |  |  |  | SQRT Square Root
[8 empty] | Purpose | Final |  |  | Chk'd by | Chengjianguo |  |  |  | CCR Control Center Room
[8 empty] | Date | 30,8,2021 |  |  | Appv'd by | LiXiangdong |  |  |  | ESP Electrostatic Precipitator
P&ID No. | Area | Motor Tag reference | Loop No. | Tag No. | System Tag No. | Service Description | Signal Tag | Instrument Type | Location | System | IO Type | Signal |  |  | IO Loc. | PV LO | PV HI | Eng. Unit | Alarm | [6 empty] | State "0" | State "1" | CV Fail Action | CV Ctrl Action | PV CHAR | From |  | Cable |  |  | To |  | Rev. | Supply | Remarks
[12 empty] | Type | Power | Wire |  |  |  |  | LLL | LL | L | Nor. | H | HH | HHH | [5 empty] | JB/Panel No. | TB | Cable Number | Cable Type | Cable Order | Cabinet No. | TB |  | By
FRESH WATER
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM140122U004M1 | TM140122SC035 | TM140122SX035 | TM140122SX035.PRO | TM FRESH WATER PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | C |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM140122U005M1 | TM140122SC036 | TM140122SX036 | TM140122SX036.PRO | TM FRESH WATER PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | C |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM140122U006M1 | TM140122SC037 | TM140122SX037 | TM140122SX037.PRO | TM SEALING WATER PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | C |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3009 | TM140122 | TM140122U007M1 | TM140122SC038 | TM140122SX038 | TM140122SX038.PRO | TM SEALING WATER PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | C |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM140322U004M1 | TM140322SC035 | TM140322SX035 | TM140322SX035.PRO | TM FRESH WATER PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | C |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM140322U005M1 | TM140322SC036 | TM140322SX036 | TM140322SX036.PRO | TM FRESH WATER PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | C |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM140322U006M1 | TM140322SC037 | TM140322SX037 | TM140322SX037.PRO | TM SEALING WATER PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | C |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM140322U007M1 | TM140322SC038 | TM140322SX038 | TM140322SX038.PRO | TM SEALING WATER PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | C |  | Common for TM14.3&4
NaOH SYSTEM
P-OKITM07-10-320-07-PID-3010 | TM140115 | TM140115U001M1 | TM140115SC014 | TM140115SX014 | TM140115SX014.PRO | NaOH DOSING PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | C |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3010 | TM140115 | TM140115U002M1 | TM140115SC015 | TM140115SX015 | TM140115SX015.PRO | NaOH DOSING PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | C |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3010 | TM140115 | TM140115U003M1 | TM140115SC016 | TM140115SX016 | TM140115SX016.PRO | NaOH DOSING PUMP 3 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | C |  | Common for TM14.1&2
P-OKITM07-10-320-07-PID-3710 | TM140315 | TM140315U001M1 | TM140315SC014 | TM140315SX014 | TM140315SX014.PRO | NaOH DOSING PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | C |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3710 | TM140315 | TM140315U002M1 | TM140315SC015 | TM140315SX015 | TM140315SX015.PRO | NaOH DOSING PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | C |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3710 | TM140315 | TM140315U003M1 | TM140315SC016 | TM140315SX016 | TM140315SX016.PRO | NaOH DOSING PUMP 3 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | C |  | Common for TM14.3&4
STEAM AND CONDENSATE SYSTEM
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM140135U005M1 | TM140135SC038 | TM140135SX038 | TM140135SX038.PRO | CONDENSATE TANK PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | C |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140135 | TM140135U006M1 | TM140135SC039 | TM140135SX039 | TM140135SX039.PRO | CONDENSATE TANK PUMP SPARE SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | C |  | Common for TM14.1,2,3&4
P-OKITM07-10-320-07-PID-3006 | TM140335 | TM140335U005M1 | TM140335SC034 | TM140335SX034 | TM140335SX034.PRO | CONDENSATE TANK PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | C |  | Common for TM14.3&4
P-OKITM07-10-320-07-PID-3006 | TM140335 | TM140335U006M1 | TM140335SC035 | TM140335SX035 | TM140335SX035.PRO | CONDENSATE TANK PUMP SPARE SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | C |  | Common for TM14.3&4

## IO Summary
I/O COUNT SUMMARY
| AI | AO | DI | DO | TOTAL | REMARK
DCS | 30 | 5 | 37 | 7 | 79 | Common Area
PLC | 4 | 2 | 0 | 0 | 6 | TM14 PRDS PLC
SUM | 34 | 7 | 37 | 7 | 85
SIS

## Definitions
P&ID No. | The P&ID drawing number where the equipment is located.
Area | The Area where the equipment is located
Loop No. | Loop Number
Tag No. | Tag Name according to APP guideline
System Tag No. | Tag name to be appeared in DCS
Service Description | Process/service description
Signal Tag | Signal Tagname
Instrument Type | Type of instrument
Location | Location of the instrument
System | in DCS, PLC or local
IO Type | Type of input or output
Signal - Type | Signal type
Signal - Power | Power for the signal
Signal - Wire | wiring configuration
IO Loc. | Input and Output location
PV LO | Range Low
PV HI | Range High
Eng. Unit | Engineering Unit
Alarm | LLL- Low Low Low, HHH- High High High etc
State "0" | For Valves, If signal is zero, what willl be the valve opening.
State "1" | For Valves, If signal is one, what willl be the valve opening.
CV fail Action | For Valves, If air fails, what willl be the valve status.
CV Control Action | For Valves, Direction of the control.
PV CHAR | Process value characteristics
Rev | Revision
Supply By | Supplier name
Remarks