## 14.2-IO Database
PMT: | [5 empty] | Design Institute: |  |  | Project No. | P-OKITM07-10 | [6 empty] | DCS I/O Database
[9 empty] | Project Name | DETAIL ENGINEERING FOR 4(FOUR) UNITS TISSUE MACHINE
[9 empty] | Doc. No. | P-OKITM07-10-320-06-LST-3355 | [7 empty] | Abbreviations
Owner: | [8 empty] | Rev. No. | 4 |  |  | Prep'd by | Dengzuijie |  |  |  | EER Electronic Equipment Room |  |  |  | SQRT Square Root
[9 empty] | Purpose | Final |  |  | Chk'd by | Chengjianguo |  |  |  | CCR Control Center Room
[9 empty] | Date | 8,30,2021 |  |  | Appv'd by | LiXiangdong |  |  |  | ESP Electrostatic Precipitator
P&ID No. | Area | JB No. | ASD No. | Loop No. | Tag No. | System Tag No. | Service Description | Signal Tag | Instrument Type | Location | System | IO Type | Signal |  |  | IO Loc. | PV LO | PV HI | Eng. Unit | Alarm | [6 empty] | State "0" | State "1" | CV Fail Action | CV Ctrl Action | PV CHAR | From |  | Cable |  |  | To |  | Rev. | Supply | Remarks
[13 empty] | Type | Power | Wire |  |  |  |  | LLL | LL | L | Nor. | H | HH | HHH | [5 empty] | JB/Panel No. | TB | Cable Number | Cable Type | Cable Order | Cabinet No. | TB |  | By
MACHINE BROKE
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD102 |  | TM140217FS001 | TM140217FS001 | TM140217FS001.L | SEALING WATER TO YANKEE PULPER PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD111 |  | TM140217FS002 | TM140217FS002 | TM140217FS002.L | SEALING WATER TO BROKE DEFLAKED CHEST PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD111 |  | TM140217FS003 | TM140217FS003 | TM140217FS003.L | SEALING WATER TO BROKE INTERIM TOWER PUMP 2 FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS005 | TM140217SV005 | TM140217SV005 | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS103 |  | TM140217HS005 | TM140217SV005.ZSC | TM140217SV005.GSC | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS103 |  | TM140217HS005 | TM140217SV005.ZSO | TM140217SV005.GSO | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS103 |  | TM140217HS005 | TM140217EV005 | TM140217EV005 | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS006 | TM140217SV006 | TM140217SV006 | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS103 |  | TM140217HS006 | TM140217SV006.ZSC | TM140217SV006.GSC | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS103 |  | TM140217HS006 | TM140217SV006.ZSO | TM140217SV006.GSO | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS103 |  | TM140217HS006 | TM140217EV006 | TM140217EV006 | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA103 |  | TM140217LC007 | TM140217LT007 | TM140217LT007.MV | YANKEE PULPER LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 5000 | mm |  | 20% | 30% |  | 80% | 90% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA103 | TM1402ASD104 | TM140217LC007 | TM140217LV007A | TM140217LV007A.OUT | YANKEE PULPER LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA103 | TM1402ASD104 | TM140217LC007 | TM140217LV007B | TM140217LV007B.OUT | YANKEE PULPER LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA103 | TM1402ASD104 | TM140217LC007 | TM140217LV007C | TM140217LV007C.OUT | YANKEE PULPER LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217EC008 | TM140217EX008 | TM140217EX008.SOF | YANKEE PULPER SHEET BREAK | EX | DCS software function | DCS | DCS |  | Software function | [25 empty] | B
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD102 |  | TM140217FS009 | TM140217FS009 | TM140217FS009.L | SEALING WATER TO YANKEE PULPER RECIRCULATION PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD102 |  | TM140217FS010 | TM140217FS010 | TM140217FS010.L | SEALING WATER TO YANKEE PULPER AGITATOR FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS011 | TM140217SV011 | TM140217SV011 | YANKEE PULPER SHOWER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS103 |  | TM140217HS011 | TM140217SV011.ZSC | TM140217SV011.GSC | YANKEE PULPER SHOWER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS103 |  | TM140217HS011 | TM140217SV011.ZSO | TM140217SV011.GSO | YANKEE PULPER SHOWER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS103 |  | TM140217HS011 | TM140217EV011 | TM140217EV011 | YANKEE PULPER SHOWER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217NC012 | TM140217NE012 |  | PULP FROM YANKEE PULPER TO BROKE INTERIM TOWER CONSISTENCY | NE | Blade Consistency Sensor | Field | [28 empty] | 0
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA103 |  | TM140217NC012 | TM140217NT012 | TM140217NT012.MV | PULP FROM YANKEE PULPER TO BROKE INTERIM TOWER CONSISTENCY | NT | Blade Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 6 | %Cs | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217FC113 | TM140217FE113 |  | DILUTITION WATER TO YANKEE PULPER FLOW | FE | Magnetic Flow Sensor | Field | DCS | [27 empty] | B
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA103 |  | TM140217FC113 | TM140217FT113 | TM140217FT113.MV | DILUTITION WATER TO YANKEE PULPER FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 3500 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA103 | TM1402ASD104 | TM140217FC113 | TM140217FV113 | TM140217FV113.OUT | DILUTITION WATER TO YANKEE PULPER FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA112 |  | TM140217LI015 | TM140217LT015 | TM140217LT015.MV | BROKE INTERIM TOWER LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 12600 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS016 | TM140217SV016 | TM140217SV016 | PULP FROM BROKE INTERIM TOWER TO BROKE INTERIM TOWER PUMP 2 ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS113 |  | TM140217HS016 | TM140217SV016.ZSC | TM140217SV016.GSC | PULP FROM BROKE INTERIM TOWER TO BROKE INTERIM TOWER PUMP 2 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS113 |  | TM140217HS016 | TM140217SV016.ZSO | TM140217SV016.GSO | PULP FROM BROKE INTERIM TOWER TO BROKE INTERIM TOWER PUMP 2 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS113 |  | TM140217HS016 | TM140217EV016 | TM140217EV016 | PULP FROM BROKE INTERIM TOWER TO BROKE INTERIM TOWER PUMP 2 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA112 | TM1402ASD113 | TM140217HC017 | TM140217HV017 | TM140217HV017.OUT | BROKE INTERIM TOWER PUMP 1 INLET DILUTION WATER CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS020 | TM140217SV020 | TM140217SV020 | PULP FROM BROKE INTERIM TOWER TO PUMP 1 ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS113 |  | TM140217HS020 | TM140217SV020.ZSC | TM140217SV020.GSC | PULP FROM BROKE INTERIM TOWER TO PUMP 1 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS113 |  | TM140217HS020 | TM140217SV020.ZSO | TM140217SV020.GSO | PULP FROM BROKE INTERIM TOWER TO PUMP 1 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS113 |  | TM140217HS020 | TM140217EV020 | TM140217EV020 | PULP FROM BROKE INTERIM TOWER TO PUMP 1 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS021 | TM140217SV021 | TM140217SV021 | HC-CLEANER FEED ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS201 |  | TM140217HS021 | TM140217SV021.ZSC | TM140217SV021.GSC | HC-CLEANER FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS201 |  | TM140217HS021 | TM140217SV021.ZSO | TM140217SV021.GSO | HC-CLEANER FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS201 |  | TM140217HS021 | TM140217EV021 | TM140217EV021 | HC-CLEANER FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS022 | TM140217SV022 | TM140217SV022 | HC-CLEANER ACCEPT ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS201 |  | TM140217HS022 | TM140217SV022.ZSC | TM140217SV022.GSC | HC-CLEANER ACCEPT ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS201 |  | TM140217HS022 | TM140217SV022.ZSO | TM140217SV022.GSO | HC-CLEANER ACCEPT ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS201 |  | TM140217HS022 | TM140217EV022 | TM140217EV022 | HC-CLEANER ACCEPT ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS023 | TM140217SV023 | TM140217SV023 | HC-CLEANER BYPASS ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS201 |  | TM140217HS023 | TM140217SV023.ZSC | TM140217SV023.GSC | HC-CLEANER BYPASS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS201 |  | TM140217HS023 | TM140217SV023.ZSO | TM140217SV023.GSO | HC-CLEANER BYPASS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS201 |  | TM140217HS023 | TM140217EV023 | TM140217EV023 | HC-CLEANER BYPASS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA201 |  | TM140217PC028 | TM140217PT028 | TM140217PT028.MV | HC-CLEANER FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA201 |  | TM140217PC029 | TM140217PT029 | TM140217PT029.MV | HC-CLEANER ACCEPT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA201 | TM1402ASD201 | TM140217PC029 | TM140217PV029 | TM140217PV029.OUT | HC-CLEANER ACCEPT PRESSURE CV SETPOINT | PV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217KS031 | TM140217KX031 | TM140217KX031.SOF | HC-CLEANER JUNK TRAP SEQUENCE | KX | DCS software function | DCS | DCS |  | Software function
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS031A | TM140217SV031A | TM140217SV031A | HC-CLEANER REJECT TOP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD203 |  | TM140217HS031A | TM140217SV031A.ZSC | TM140217SV031A.GSC | HC-CLEANER REJECT TOP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD203 |  | TM140217HS031A | TM140217SV031A.ZSO | TM140217SV031A.GSO | HC-CLEANER REJECT TOP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD203 | TM1402ASD202 | TM140217HS031A | TM140217EV031A | TM140217EV031A | HC-CLEANER REJECT TOP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS031B | TM140217SV031B | TM140217SV031B | HC-CLEANER REJECT BOTTOM ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD203 |  | TM140217HS031B | TM140217SV031B.ZSC | TM140217SV031B.GSC | HC-CLEANER REJECT BOTTOM ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD203 |  | TM140217HS031B | TM140217SV031B.ZSO | TM140217SV031B.GSO | HC-CLEANER REJECT BOTTOM ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD203 | TM1402ASD202 | TM140217HS031B | TM140217EV031B | TM140217EV031B | HC-CLEANER REJECT BOTTOM ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS031C | TM140217SV031C | TM140217SV031C | HC-CLEANER REJECT TOP FLUSHING ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD203 |  | TM140217HS031C | TM140217SV031C.ZSC | TM140217SV031C.GSC | HC-CLEANER REJECT TOP FLUSHING ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD203 |  | TM140217HS031C | TM140217SV031C.ZSO | TM140217SV031C.GSO | HC-CLEANER REJECT TOP FLUSHING ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD203 | TM1402ASD202 | TM140217HS031C | TM140217EV031C | TM140217EV031C | HC-CLEANER REJECT TOP FLUSHING ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS031D | TM140217SV031D | TM140217SV031D | HC-CLEANER REJECT BOTTOM FLUSHING ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD203 |  | TM140217HS031D | TM140217SV031D.ZSC | TM140217SV031D.GSC | HC-CLEANER REJECT BOTTOM FLUSHING ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD203 |  | TM140217HS031D | TM140217SV031D.ZSO | TM140217SV031D.GSO | HC-CLEANER REJECT BOTTOM FLUSHING ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD203 | TM1402ASD202 | TM140217HS031D | TM140217EV031D | TM140217EV031D | HC-CLEANER REJECT BOTTOM FLUSHING ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS031E | TM140217SV031E | TM140217SV031E | HC-CLEANER REJECT EXHAUSTING ON/OFF VALVE OPENED | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD203 |  | TM140217HS031E | TM140217SV031E.ZSC | TM140217SV031E.GSC | HC-CLEANER REJECT EXHAUSTING ON/OFF VALVE OPENED CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD203 |  | TM140217HS031E | TM140217SV031E.ZSO | TM140217SV031E.GSO | HC-CLEANER REJECT EXHAUSTING ON/OFF VALVE OPENED OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD203 | TM1402ASD202 | TM140217HS031E | TM140217EV031E | TM140217EV031E | HC-CLEANER REJECT EXHAUSTING ON/OFF VALVE OPENED SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA101 |  | TM140217LC032 | TM140217LT032 | TM140217LT032.MV | THICKENER BROKE TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS034 | TM140217SV034 | TM140217SV034 | BROKE DEFLAKER FLUSHING ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS203 |  | TM140217HS034 | TM140217SV034.ZSC | TM140217SV034.GSC | BROKE DEFLAKER FLUSHING ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS203 |  | TM140217HS034 | TM140217SV034.ZSO | TM140217SV034.GSO | BROKE DEFLAKER FLUSHING ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS203 |  | TM140217HS034 | TM140217EV034 | TM140217EV034 | BROKE DEFLAKER FLUSHING ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS035 | TM140217SV035 | TM140217SV035 | BROKE DEFLAKER FEED ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS203 |  | TM140217HS035 | TM140217SV035.ZSC | TM140217SV035.GSC | BROKE DEFLAKER FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS203 |  | TM140217HS035 | TM140217SV035.ZSO | TM140217SV035.GSO | BROKE DEFLAKER FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS203 |  | TM140217HS035 | TM140217EV035 | TM140217EV035 | BROKE DEFLAKER FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS036 | TM140217SV036 | TM140217SV036 | BROKE DEFLAKER ACCEPT ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS203 |  | TM140217HS036 | TM140217SV036.ZSC | TM140217SV036.GSC | BROKE DEFLAKER ACCEPT ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS203 |  | TM140217HS036 | TM140217SV036.ZSO | TM140217SV036.GSO | BROKE DEFLAKER ACCEPT ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS203 |  | TM140217HS036 | TM140217EV036 | TM140217EV036 | BROKE DEFLAKER ACCEPT ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS037 | TM140217SV037 | TM140217SV037 | BROKE DEFLAKER BYPASS ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS203 |  | TM140217HS037 | TM140217SV037.ZSC | TM140217SV037.GSC | BROKE DEFLAKER BYPASS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS203 |  | TM140217HS037 | TM140217SV037.ZSO | TM140217SV037.GSO | BROKE DEFLAKER BYPASS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS203 |  | TM140217HS037 | TM140217EV037 | TM140217EV037 | BROKE DEFLAKER BYPASS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA201 |  | TM140217PI038 | TM140217PT038 | TM140217PT038.MV | BROKE DEFLAKER FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217FC039 | TM140217FE039 |  | STOCK TO BROKE DEFLAKED CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA101 |  | TM140217FC039 | TM140217FT039 | TM140217FT039.MV | STOCK TO BROKE DEFLAKED CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 720 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA101 | TM1402ASD101 | TM140217FC039 | TM140217FV039 | TM140217FV039.OUT | STOCK TO BROKE DEFLAKED CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217WC040 | TM140217WX040 | TM140217WX040.SOF | BROKE DEFLAKER SEC SETPOINT | WX | DCS software function | DCS | DCS |  | Software function
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD201 |  | TM140217FS041 | TM140217FS041 | TM140217FS041.L | SEALING WATER TO BROKE DEFLAKER FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA112 |  | TM140217LC042 | TM140217LT042 | TM140217LT042.MV | BROKE DEFLAKED CHEST LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA112 | TM1402ASD112 | TM140217LC042 | TM140217LV042 | TM140217LV042.OUT | BROKE DEFLAKED CHEST LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217NC044 | TM140217NE044 |  | DEFLAKED BROKE TO MIXING CHEST CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230 VAC | [24 empty] | B
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA112 |  | TM140217NC044 | TM140217NT044 | TM140217NT044.MV | DEFLAKED BROKE TO MIXING CHEST CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 6 | %Cs | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD111 |  | TM140217NC044 | TM140217NS044 | TM140217NS044.MV | DEFLAKED BROKE TO MIXING CHEST CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA112 | TM1402ASD112 | TM140217NC044 | TM140217NV044 | TM140217NV044.OUT | DEFLAKED BROKE TO MIXING CHEST CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS046 | TM140217SV046 | TM140217SV046 | BROKE DEFLAKED CHEST OUTLET ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS112 |  | TM140217HS046 | TM140217SV046.ZSC | TM140217SV046.GSC | BROKE DEFLAKED CHEST OUTLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS112 |  | TM140217HS046 | TM140217SV046.ZSO | TM140217SV046.GSO | BROKE DEFLAKED CHEST OUTLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS112 |  | TM140217HS046 | TM140217EV046 | TM140217EV046 | BROKE DEFLAKED CHEST OUTLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS048 | TM140217SV048 | TM140217SV048 | SEALING WATER TO YANKEE PULPER AGITATOR ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS103 |  | TM140217HS048 | TM140217SV048.ZSC | TM140217SV048.GSC | SEALING WATER TO YANKEE PULPER AGITATOR ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS103 |  | TM140217HS048 | TM140217SV048.ZSO | TM140217SV048.GSO | SEALING WATER TO YANKEE PULPER AGITATOR ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS103 |  | TM140217HS048 | TM140217EV048 | TM140217EV048 | SEALING WATER TO YANKEE PULPER AGITATOR ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA112 |  | TM140217PC049 | TM140217PT049 | TM140217PT049.MV | BROKE DEFLAKED CHEST PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 4 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS051 | TM140217SV051 | TM140217SV051 | SEALING WATER TO BROKE DEFLAKER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS203 |  | TM140217HS051 | TM140217SV051.ZSC | TM140217SV051.GSC | SEALING WATER TO BROKE DEFLAKER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS203 |  | TM140217HS051 | TM140217SV051.ZSO | TM140217SV051.GSO | SEALING WATER TO BROKE DEFLAKER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS203 |  | TM140217HS051 | TM140217EV051 | TM140217EV051 | SEALING WATER TO BROKE DEFLAKER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA201 |  | TM140217PI052 | TM140217PT052 | TM140217PT052.MV | BROKE DEFLAKER ACCEPT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD201 |  | TM140217TS053 | TM140217TS053 | TM140217TS053.H | BROKE DEFLAKER OUTLET TEMPERATURE HIGH | TS | Temperature switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [7 empty] | Temp. High | Not Temp. High | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS055 | TM140217SV055 | TM140217SV055 | SHOWER WATER TO YANKEE PULPER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS103 |  | TM140217HS055 | TM140217SV055.ZSC | TM140217SV055.GSC | SHOWER WATER TO YANKEE PULPER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS103 |  | TM140217HS055 | TM140217SV055.ZSO | TM140217SV055.GSO | SHOWER WATER TO YANKEE PULPER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS103 |  | TM140217HS055 | TM140217EV055 | TM140217EV055 | SHOWER WATER TO YANKEE PULPER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA112 | TM1402ASD113 | TM140217HC056 | TM140217HV056 | TM140217HV056.OUT | BROKE INTERIM TOWER PUMP OUTLET CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217KS057 | TM140217SV057A | TM140217SV057A | BROKE THICKENER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS201 |  | TM140217KS057 | TM140217SV057A.ZSC | TM140217SV057A.GSC | BROKE THICKENER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS201 |  | TM140217KS057 | TM140217SV057A.ZSO | TM140217SV057A.GSO | BROKE THICKENER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS201 |  | TM140217KS057 | TM140217EV057A | TM140217EV057A | BROKE THICKENER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD201 | TM1402ASD201 | TM140217KS057 | TM140217EV057B | TM140217EV057B | BROKE THICKENER ON/OFF VALVE CLOSED SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD201 | TM1402ASD201 | TM140217KS057 | TM140217EV057C | TM140217EV057C | BROKE THICKENER ON/OFF VALVE OPENED SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS058 | TM140217SV058 | TM140217SV058 | BROKE THICKENER TANK PUMP INLET ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS101 |  | TM140217HS058 | TM140217SV058.ZSC | TM140217SV058.GSC | BROKE THICKENER TANK PUMP INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS101 |  | TM140217HS058 | TM140217SV058.ZSO | TM140217SV058.GSO | BROKE THICKENER TANK PUMP INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS101 |  | TM140217HS058 | TM140217EV058 | TM140217EV058 | BROKE THICKENER TANK PUMP INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS061 | TM140217SV061 | TM140217SV061 | BROKE DEFLAKED CHEST PUMP OUTLET TO MIXING CHEST ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS112 |  | TM140217HS061 | TM140217SV061.ZSC | TM140217SV061.GSC | BROKE DEFLAKED CHEST PUMP OUTLET TO MIXING CHEST ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS112 |  | TM140217HS061 | TM140217SV061.ZSO | TM140217SV061.GSO | BROKE DEFLAKED CHEST PUMP OUTLET TO MIXING CHEST ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS112 |  | TM140217HS061 | TM140217EV061 | TM140217EV061 | BROKE DEFLAKED CHEST PUMP OUTLET TO MIXING CHEST ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217HS062 | TM140217SV062 | TM140217SV062 | BROKE DEFLAKED CHEST PUMP OUTLET TO BROKE THICKENER TANK ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS112 |  | TM140217HS062 | TM140217SV062.ZSC | TM140217SV062.GSC | BROKE DEFLAKED CHEST PUMP OUTLET TO BROKE THICKENER TANK ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS112 |  | TM140217HS062 | TM140217SV062.ZSO | TM140217SV062.GSO | BROKE DEFLAKED CHEST PUMP OUTLET TO BROKE THICKENER TANK ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBS112 |  | TM140217HS062 | TM140217EV062 | TM140217EV062 | BROKE DEFLAKED CHEST PUMP OUTLET TO BROKE THICKENER TANK ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 |  |  | TM140217NC091 | TM140217NE091 |  | BROKE THICKENER TANK PUMP OUTLET CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230 VAC | [24 empty] | B
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA101 |  | TM140217NC091 | TM140217NT091 | TM140217NT091.MV | BROKE THICKENER TANK PUMP OUTLET CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 6 | %Cs | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD101 |  | TM140217NC091 | TM140217NS091 | TM140217NS091.MV | BROKE THICKENER TANK PUMP OUTLET CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBA101 | TM1402ASD101 | TM140217NC091 | TM140217NV091 | TM140217NV091.OUT | BROKE THICKENER TANK PUMP OUTLET CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD102 |  | TM140217XS093 | TM140217XS093A | TM140217EX008A | SHEET BREAK | XS | Web break signals | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Web break | Not Web break | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD102 |  | TM140217XS093 | TM140217XS093B | TM140217EX008B | SHEET BREAK | XS | Web break signals | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Web break | Not Web break | [10 empty] | 1
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM1402JBD101 |  | TM140217FS095 | TM140217FS095 | TM140217FS095.L | SEALING WATER TO BROKE BROKE THICKENER TANK PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
STOCK APPROACH
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220FC001 | TM140220FE001 |  | NBKP#3 REFINED TOWER #1 PUMP TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS | [27 empty] | B
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 |  | TM140220FC001 | TM140220FT001 | TM140220FT001.MV | NBKP#3 REFINED TOWER #1 PUMP TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1000 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 | TM1402ASD111 | TM140220FC001 | TM140220FV001 | TM140220FV001.OUT | NBKP#3 REFINED TOWER #1 PUMP TO MIXING CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220FC002 | TM140220FE002 |  | LBKP 2 INTERMEDIATE TOWER PUMP TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 |  | TM140220FC002 | TM140220FT002 | TM140220FT002.MV | LBKP 2 INTERMEDIATE TOWER PUMP TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 2700 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 | TM1402ASD111 | TM140220FC002 | TM140220FV002 | TM140220FV002.OUT | LBKP 2 INTERMEDIATE TOWER PUMP TO MIXING CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220FC003 | TM140220FE003 |  | BROKE DEFLAKED CHEST PUMP TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 |  | TM140220FC003 | TM140220FT003 | TM140220FT003.MV | BROKE DEFLAKED CHEST PUMP TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 720 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 | TM1402ASD111 | TM140220FC003 | TM140220FV003 | TM140220FV003.OUT | BROKE DEFLAKED CHEST PUMP TO MIXING CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220FC004 | TM140220FE004 |  | SP2 BROKE TOWER PUMP TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 |  | TM140220FC004 | TM140220FT004 | TM140220FT004.MV | SP2 BROKE TOWER PUMP TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1100 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 | TM1402ASD111 | TM140220FC004 | TM140220FV004 | TM140220FV004.OUT | SP2 BROKE TOWER PUMP TO MIXING CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220FC005 | TM140220FE005 |  | RECOVERED STOCK PUMP TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 |  | TM140220FC005 | TM140220FT005 | TM140220FT005.MV | RECOVERED STOCK PUMP TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1800 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220HS006 | TM140220SV006 | TM140220SV006 | SWEETENER PUMP INLET ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS111 |  | TM140220HS006 | TM140220SV006.ZSC | TM140220SV006.GSC | SWEETENER PUMP INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS111 |  | TM140220HS006 | TM140220SV006.ZSO | TM140220SV006.GSO | SWEETENER PUMP INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS111 |  | TM140220HS006 | TM140220EV006 | TM140220EV006 | SWEETENER PUMP INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 |  | TM140220LC008 | TM140220LT008 | TM140220LT008.MV | MIXING CHEST LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 5000 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220HS009 | TM140220SV009 | TM140220SV009 | DILUTION WATER TO SWEETENER PUMP INLET ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS111 |  | TM140220HS009 | TM140220SV009.ZSC | TM140220SV009.GSC | DILUTION WATER TO SWEETENER PUMP INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS111 |  | TM140220HS009 | TM140220SV009.ZSO | TM140220SV009.GSO | DILUTION WATER TO SWEETENER PUMP INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS111 |  | TM140220HS009 | TM140220EV009 | TM140220EV009 | DILUTION WATER TO SWEETENER PUMP INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD111 |  | TM140220FS010 | TM140220FS010 | TM140220FS010.L | SEALING WATER TO SWEETENER PUMP FLOW | FS | Flow Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220HS011 | TM140220SV011 | TM140220SV011 | MIXING CHEST DISCHAGE ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS111 |  | TM140220HS011 | TM140220SV011.ZSC | TM140220SV011.GSC | MIXING CHEST DISCHAGE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS111 |  | TM140220HS011 | TM140220SV011.ZSO | TM140220SV011.GSO | MIXING CHEST DISCHAGE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS111 |  | TM140220HS011 | TM140220EV011 | TM140220EV011 | MIXING CHEST DISCHAGE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220NC012 | TM140220NE012 |  | MIXING CHEST PUMP OUTLET CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230 VAC | [24 empty] | B
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 |  | TM140220NC012 | TM140220NT012 | TM140220NT012.MV | MIXING CHEST PUMP OUTLET CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 6 | %C | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD111 |  | TM140220NC012 | TM140220NS012 | TM140220NS012.MV | MIXING CHEST PUMP OUTLET CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 | TM1402ASD111 | TM140220NC012 | TM140220NV012 | TM140220NV012.OUT | MIXING CHEST PUMP OUTLET CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD111 |  | TM140220FS014 | TM140220FS014 | TM140220FS014.L | SEALING WATER TO MIXING CHEST PUMP 1 FLOW | FS | Flow Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220FC015 | TM140220FE015 |  | NBKP#3 REFINED TOWER #2 PUMP1 TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS | [27 empty] | B
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 |  | TM140220FC015 | TM140220FT015 | TM140220FT015.MV | NBKP#3 REFINED TOWER #2 PUMP1 TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1000 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 | TM1402ASD111 | TM140220FC015 | TM140220FV015 | TM140220FV015.OUT | NBKP#3 REFINED TOWER #2 PUMP1 TO MIXING CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA201 |  | TM140220PI021 | TM140220PT021 | TM140220PT021.MV | TICKLER REFINER FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220CB01 |  | TM140220PI021 | TM140220PI021 | TM140220PI021.IND | TICKLER REFINER FEED PRESSURE | PI | Local digital indicator | Field | DCS | AO | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA201 |  | TM140220PI022 | TM140220PT022 | TM140220PT022.MV | TICKLER REFINER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220CB01 |  | TM140220PI022 | TM140220PI022 | TM140220PI022.IND | TICKLER REFINER OUTLET PRESSURE | PI | Local digital indicator | Field | DCS | AO | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220HS024 | TM140220SV024 | TM140220SV024 | TICKLER REFINER FEED ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS204 |  | TM140220HS024 | TM140220SV024.ZSC | TM140220SV024.GSC | TICKLER REFINER FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS204 |  | TM140220HS024 | TM140220SV024.ZSO | TM140220SV024.GSO | TICKLER REFINER FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS204 |  | TM140220HS024 | TM140220EV024 | TM140220EV024 | TICKLER REFINER FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220HS025 | TM140220SV025 | TM140220SV025 | TICKLER REFINER ACCEPT ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS204 |  | TM140220HS025 | TM140220SV025.ZSC | TM140220SV025.GSC | TICKLER REFINER ACCEPT ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS204 |  | TM140220HS025 | TM140220SV025.ZSO | TM140220SV025.GSO | TICKLER REFINER ACCEPT ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS204 |  | TM140220HS025 | TM140220EV025 | TM140220EV025 | TICKLER REFINER ACCEPT ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220HS026 | TM140220SV026 | TM140220SV026 | TICKLER REFINER BYPASS ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS204 |  | TM140220HS026 | TM140220SV026.ZSC | TM140220SV026.GSC | TICKLER REFINER BYPASS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS204 |  | TM140220HS026 | TM140220SV026.ZSO | TM140220SV026.GSO | TICKLER REFINER BYPASS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS204 |  | TM140220HS026 | TM140220EV026 | TM140220EV026 | TICKLER REFINER BYPASS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220HS027 | TM140220SV027 | TM140220SV027 | DILUTION WATER TO TICKLER REFINER FEED ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS204 |  | TM140220HS027 | TM140220SV027.ZSC | TM140220SV027.GSC | DILUTION WATER TO TICKLER REFINER FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS204 |  | TM140220HS027 | TM140220SV027.ZSO | TM140220SV027.GSO | DILUTION WATER TO TICKLER REFINER FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS204 |  | TM140220HS027 | TM140220EV027 | TM140220EV027 | DILUTION WATER TO TICKLER REFINER FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220HS028 | TM140220SV028 | TM140220SV028 | SEALING WATER TO TICKLER REFINER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS204 |  | TM140220HS028 | TM140220SV028.ZSC | TM140220SV028.GSC | SEALING WATER TO TICKLER REFINER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS204 |  | TM140220HS028 | TM140220SV028.ZSO | TM140220SV028.GSO | SEALING WATER TO TICKLER REFINER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS204 |  | TM140220HS028 | TM140220EV028 | TM140220EV028 | SEALING WATER TO TICKLER REFINER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD202 |  | TM140220FS029 | TM140220FS029 | TM140220FS029.L | SEALING WATER TO TICKLER REFINER FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220TIZ030 | TM140220TE030 |  | TICKLER REFINER OUTLET TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | B | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA201 |  | TM140220TIZ030 | TM140220TT030 | TM140220TT030.MV | TICKLER REFINER OUTLET TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD202 |  | TM140220TIZ030 | TM140220TS030 | TM140220TS030.H | TICKLER REFINER OUTLET TEMPERATURE HIGH | TS | Temperature switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 150 | ˚C | [7 empty] | Temp. High | Not Temp. High | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD202 |  | TM140220GS031 | TM140220GS031.A | TM140220GS031.A.START | TICKLER REFINER FILLINGS POSITION START | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Start | Start | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD202 |  | TM140220GS031 | TM140220GS031.B | TM140220GS031.B.OPEN | TICKLER REFINER FILLINGS POSITION OPEN | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD202 |  | TM140220GS031 | TM140220GS031.C | TM140220GS031.C.SAF | TICKLER REFINER FILLINGS POSITION SAFETY | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Safety | Safety | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 | MCC |  | TM140220EC033 | TM140220ET033 | TM140220ET033.MV | TICKLER REFINER POWER | ET | Power transmitter | MCC | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | MCC | 0 | 355 | kW | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220CB01 |  | TM140220EC033 | TM140220EI033 | TM140220EI033.IND | TICKLER REFINER POWER | EI | Local digital indicator | Field | DCS | AO | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 100 | % | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220FC034 | TM140220FE034 |  | TICKLER REFINER TO MACHINE CHEST FLOW | FE | Magnetic flow Sensor | Field
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 |  | TM140220FC034 | TM140220FT034 | TM140220FT034.MV | TICKLER REFINER TO MACHINE CHEST FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 3600 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 | TM1402ASD111 | TM140220FC034 | TM140220FV034 | TM140220FV034.OUT | TICKLER REFINER TO MACHINE CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220FC035 | TM140220FE035 |  | TICKLER REFINER RECIRCULATION FLOW | FE | Magnetic flow Sensor | Field
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 |  | TM140220FC035 | TM140220FT035 | TM140220FT035.MV | TICKLER REFINER RECIRCULATION FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1800 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 | TM1402ASD111 | TM140220FC035 | TM140220FV035 | TM140220FV035.OUT | TICKLER REFINER RECIRCULATION FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220WC036 | TM140220WX036 | TM140220WX036.SOF | TICKLER REFINER PRODUCTION | WX | DCS software function | DCS | DCS |  | Software function
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220AI037 | TM140220AE037 |  | TICKLER REFINER FREENESS | AE | Freeness sensor | Field
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 |  | TM140220AI037 | TM140220AT037 | TM140220AT037.MV | TICKLER REFINER FREENESS | AT | Freeness transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 15 | 750 | ml CSF | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD111 |  | TM140220AI037 | TM140220AS037 | TM140220AS037.MV | TICKLER REFINER FREENESS | AS | Freeness transmitter Stop Sampling | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220XS038 | TM140220CB01 | TM110011CB01 | TICKLER REFINER CONTROL | CB | Local Control Box | Field |  |  |  | 230 VAC | [24 empty] | 4
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220CB01 |  | TM140220XS038 | TM140220H11 038 | TM140220H11 038.RUN/F | TICKLER REFINER MOTOR RUN / FAULT | H1 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Run | Run | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220CB01 |  | TM140220XS038 | TM140220H21 038 | TM140220H21 038.L/F | TICKLER REFINER LOAD / FAULT | H2 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Load | Load | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220CB01 |  | TM140220XS038 | TM140220H22 038 | TM140220H22 038.REL/F | TICKLER REFINER RELEASE / FAULT | H2 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Release | Release | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220CB01 |  | TM140220XS038 | TM140220H23 038 | TM140220H23 038.FAULT | TICKLER REFINER FAULT | H2 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Fault | Fault | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220CB01 |  | TM140220XS038 | TM140220S10 038 | TM140220S10 038.ESTOP | TICKLER REFINER PANEL E - STOP | S1 | E - Stop Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | E - Stop | Not E - Stop | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220CB01 |  | TM140220XS038 | TM140220S11 038 | TM140220S11 038.START | TICKLER REFINER START | S1 | Illuminated Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Start | Start | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220CB01 |  | TM140220XS038 | TM140220S12 038 | TM140220S12 038.STOP | TICKLER REFINER STOP | S1 | Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Stop | Not Stop | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220CB01 |  | TM140220XS038 | TM140220S20 038 | TM140220S20 038.L/D | OPERATING MODE SELECT SWITCH - LOCAL/DCS | S2 | Select Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | DCS | Local | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220CB01 |  | TM140220XS038 | TM140220S21 038 | TM140220S21 038.LOAD | TICKLER REFINER LOAD | S2 | Illuminated Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Load | Load | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220CB01 |  | TM140220XS038 | TM140220S22 038 | TM140220S22 038.RELEASE | TICKLER REFINER RELEASE | S2 | Illuminated Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Release | Release | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220CB01 |  | TM140220XS038 | TM140220S23 038 | TM140220S23 038.FAST | TICKLER REFINER FAST | S2 | Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Fast | Fast | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220CB01 |  | TM140220XS038 | TM140220S24 038 | TM140220S24 038.TEST | TICKLER REFINER CB LAMP TEST | S2 | Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Lamp Test | Lamp Test | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220EC039 | TM140220EX039 | TM140220EX039.SOF | TICKLER REFINER POWER | EX | DCS software function | DCS | DCS |  | Software function | [25 empty] | B
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 |  | TM140220PC045 | TM140220PT045 | TM140220PT045.MV | SWEETENER PUMP OUTLET OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 |  | TM140220LC051 | TM140220LT051 | TM140220LT051.MV | MACHINE CHEST LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 5000 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220HS052 | TM140220SV052 | TM140220SV052 | MACHINE CHEST DISCHAGE ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS112 |  | TM140220HS052 | TM140220SV052.ZSC | TM140220SV052.GSC | MACHINE CHEST DISCHAGE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS112 |  | TM140220HS052 | TM140220SV052.ZSO | TM140220SV052.GSO | MACHINE CHEST DISCHAGE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS112 |  | TM140220HS052 | TM140220EV052 | TM140220EV052 | MACHINE CHEST DISCHAGE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220NC053 | TM140220NE053 |  | MACHINE CHEST PUMP OUTLET CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230 VAC
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 |  | TM140220NC053 | TM140220NT053 | TM140220NT053.MV | MACHINE CHEST PUMP OUTLET CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 6 | %C | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD111 |  | TM140220NC053 | TM140220NS053 | TM140220NS053.MV | MACHINE CHEST PUMP OUTLET CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 | TM1402ASD111 | TM140220NC053 | TM140220NV053 | TM140220NV053.OUT | MACHINE CHEST PUMP OUTLET CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA111 |  | TM140220PC054 | TM140220PT054 | TM140220PT054.MV | MACHINE CHEST PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220FC055 | TM140220FE055 |  | MACHINE CHEST PUMP OUTLET FLOW | FE | Magnetic flow Sensor | Field
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA102 |  | TM140220FC055 | TM140220FT055 | TM140220FT055.MV | MACHINE CHEST PUMP OUTLET FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 3600 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220FC055 | TM140220FV055 | TM140220FV055.OUT | MACHINE CHEST PUMP OUTLET FLOW CV SETPOINT | FV | Basic Weight Valve | [29 empty] | C
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA102 |  | TM140220FC055 | TM140220FY055 | TM140220FY055.MV | MACHINE CHEST PUMP OUTLET FLOW CV POSITION FEEDBACK | FY | Valve Position Feedback | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD101 |  | TM140220FC055 | TM140220FV055.ZSC | TM140220FV055.GSC | MACHINE CHEST PUMP OUTLET FLOW CV CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD101 |  | TM140220FC055 | TM140220FV055.ZSO | TM140220FV055.GSO | MACHINE CHEST PUMP OUTLET FLOW CV OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD101 |  | TM140220FC055 | TM140220FV055.STP | TM140220FV055.STP | MACHINE CHEST PUMP OUTLET FLOW CV CLOSE COMMAND | STP | Close Command | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [11 empty] | Close | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD101 |  | TM140220FC055 | TM140220FV055.STO | TM140220FV055.STO | MACHINE CHEST PUMP OUTLET FLOW CV OPEN COMMAND | STO | Open Command | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [11 empty] | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD111 |  | TM140220FS057 | TM140220FS057 | TM140220FS057.L | SEALING WATER TO MACHINE CHEST PUMP 1 FLOW | FS | Flow Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA202 |  | TM140220LI061 | TM140220LT061 | TM140220LT061.MV | SILO LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3000 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220HS062 | TM140220SV062 | TM140220SV062 | WHITE WATER TO SILO ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS205 |  | TM140220HS062 | TM140220SV062.ZSC | TM140220SV062.GSC | WHITE WATER TO SILO ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS205 |  | TM140220HS062 | TM140220SV062.ZSO | TM140220SV062.GSO | WHITE WATER TO SILO ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS205 |  | TM140220HS062 | TM140220EV062 | TM140220EV062 | WHITE WATER TO SILO ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140235TC020 | TM140235TE020 |  | SILO TEMPERATURE | TE | Temperature Sensor | Field
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA202 |  | TM140235TC020 | TM140235TT020 | TM140235TT020.MV | SILO TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA202 | TM1402ASD201 | TM140235TC020 | TM140235TV020 | TM140235TV020.OUT | SILO TEMPERATURE CV SETPOINT | TV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220AI064 | TM140220AE064 |  | SILO CHANNEL OVERFLOW PARTICLE CHARGE DETECT | AE | PCD sensor | Field | DCS
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA202 |  | TM140220AI064 | TM140220AT064 | TM140220AT064.MV | SILO CHANNEL OVERFLOW PARTICLE CHARGE DETECT | AT | PCD transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | -150 | -30 | µEQ/l | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD202 |  | TM140220AI064 | TM140220AS064 | TM140220AS064.INT | SILO CHANNEL OVERFLOW PARTICLE CHARGE INTERLOCK | AS | PCD transmitter Stop Sampling | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220AC065 | TM140220AE065 |  | SILO PH | AE | pH Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA202 |  | TM140220AC065 | TM140220AT065 | TM140220AT065.MV | SILO PH | AT | pH Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 14 | Ph | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220HS066 | TM140220SV066 | TM140220SV066 | MACHINE CHEST PUMP OUTLET TO SILO ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 0
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS102 |  | TM140220HS066 | TM140220SV066.ZSC | TM140220SV066.GSC | MACHINE CHEST PUMP OUTLET TO SILO ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS102 |  | TM140220HS066 | TM140220SV066.ZSO | TM140220SV066.GSO | MACHINE CHEST PUMP OUTLET TO SILO ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS102 |  | TM140220HS066 | TM140220EV066 | TM140220EV066 | MACHINE CHEST PUMP OUTLET TO SILO ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220HS067 | TM140220SV067 | TM140220SV067 | MACHINE CHEST PUMP OUTLET TO RECOVERED STOCK CHEST ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 0
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS102 |  | TM140220HS067 | TM140220SV067.ZSC | TM140220SV067.GSC | MACHINE CHEST PUMP OUTLET TO RECOVERED STOCK CHEST ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS102 |  | TM140220HS067 | TM140220SV067.ZSO | TM140220SV067.GSO | MACHINE CHEST PUMP OUTLET TO RECOVERED STOCK CHEST ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS102 |  | TM140220HS067 | TM140220EV067 | TM140220EV067 | MACHINE CHEST PUMP OUTLET TO RECOVERED STOCK CHEST ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220HS072 | TM140220SV072 | TM140220SV072 | SEALING WATER TO FAN PUMP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS101 |  | TM140220HS072 | TM140220SV072.ZSC | TM140220SV072.GSC | SEALING WATER TO FAN PUMP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS101 |  | TM140220HS072 | TM140220SV072.ZSO | TM140220SV072.GSO | SEALING WATER TO FAN PUMP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS101 |  | TM140220HS072 | TM140220EV072 | TM140220EV072 | SEALING WATER TO FAN PUMP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD101 |  | TM140220FS073 | TM140220FS073 | TM140220FS073.L | SEALING WATER TO FAN PUMP FLOW L A | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220HS075 | TM140220SV075 | TM140220SV075 | FAN PUMP OUTLET ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS101 |  | TM140220HS075 | TM140220SV075.ZSC | TM140220SV075.GSC | FAN PUMP OUTLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS101 |  | TM140220HS075 | TM140220SV075.ZSO | TM140220SV075.GSO | FAN PUMP OUTLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS101 |  | TM140220HS075 | TM140220EV075 | TM140220EV075 | FAN PUMP OUTLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA102 | TM1402ASD102 | TM140220HC078 | TM140220HV078 | TM140220HV078.OUT | 1ST STAGE APPROACH SCREEN REJECT CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220XI079 | TM140220XE079 |  | 1ST STAGE APPROACH SCREEN MOTOR VIBRATION 1 | XE | Vibration sensor | Field | [28 empty] | C | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA102 |  | TM140220XI079 | TM140220XT079 | TM140220XT079.MV | 1ST STAGE APPROACH SCREEN MOTOR VIBRATION 1 | XT | Vibration transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | [22 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA102 |  | TM140220PI081 | TM140220PT081 | TM140220PT081.MV | 1ST STAGE APPROACH SCREEN FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA102 |  | TM140220PI082 | TM140220PT082 | TM140220PT082.MV | 1ST STAGE APPROACH SCREEN ACCEPT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220PDI083 | TM140220PDX083 | TM140220PDX083.SOF | 1ST STAGE APPROACH SCREEN DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220FI084 | TM140220FE084 |  | 1ST STAGE APPROACH SCREEN REJECT FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | B
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA102 |  | TM140220FI084 | TM140220FT084 | TM140220FT084.MV | 1ST STAGE APPROACH SCREEN REJECT FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 2000 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220HS085 | TM140220SV085 | TM140220SV085 | FROM 1ST STAGE APPROACH SCREENTO SILO CHANNEL ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS101 |  | TM140220HS085 | TM140220SV085.ZSC | TM140220SV085.GSC | FROM 1ST STAGE APPROACH SCREENTO SILO CHANNEL ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS101 |  | TM140220HS085 | TM140220SV085.ZSO | TM140220SV085.GSO | FROM 1ST STAGE APPROACH SCREENTO SILO CHANNEL ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS101 |  | TM140220HS085 | TM140220EV085 | TM140220EV085 | FROM 1ST STAGE APPROACH SCREENTO SILO CHANNEL ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220HS086 | TM140220SV086 | TM140220SV086 | SEALING WATER TO 1ST STAGE APPROACH SCREEN ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS101 |  | TM140220HS086 | TM140220SV086.ZSC | TM140220SV086.GSC | SEALING WATER TO 1ST STAGE APPROACH SCREEN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS101 |  | TM140220HS086 | TM140220SV086.ZSO | TM140220SV086.GSO | SEALING WATER TO 1ST STAGE APPROACH SCREEN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS101 |  | TM140220HS086 | TM140220EV086 | TM140220EV086 | SEALING WATER TO 1ST STAGE APPROACH SCREEN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD101 |  | TM140220FS087 | TM140220FS087 | TM140220FS087.L | SEALING WATER TO 1ST STAGE APPROACH SCREEN FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA201 |  | TM140220PI091 | TM140220PT091 | TM140220PT091.MV | 2ND STAGE APPROACH SCREEN FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA201 |  | TM140220PI092 | TM140220PT092 | TM140220PT092.MV | 2ND STAGE APPROACH SCREEN ACCEPT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220PDI093 | TM140220PDX093 | TM140220PDX093.SOF | 2ND STAGE APPROACH SCREEN DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220KC094 | TM140220SV094 | TM140220SV094 | 2ND STAGE APPROACH SCREEN REJECT ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD202 |  | TM140220KC094 | TM140220SV094.ZSC | TM140220SV094.GSC | 2ND STAGE APPROACH SCREEN REJECT ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD202 |  | TM140220KC094 | TM140220SV094.ZSO | TM140220SV094.GSO | 2ND STAGE APPROACH SCREEN REJECT ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD202 | TM1402ASD201 | TM140220KC094 | TM140220EV094 | TM140220EV094 | 2ND STAGE APPROACH SCREEN REJECT ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA201 | TM1402ASD201 | TM140220HC095 | TM140220HV095 | TM140220HV095.OUT | FROM 2ND STAGE APPROACH SCREEN TO SILO CHANNEL CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220HS096 | TM140220SV096 | TM140220SV096 | SEALING WATER TO 2ND STAGE APPROACH SCREEN ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS203 |  | TM140220HS096 | TM140220SV096.ZSC | TM140220SV096.GSC | SEALING WATER TO 2ND STAGE APPROACH SCREEN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS203 |  | TM140220HS096 | TM140220SV096.ZSO | TM140220SV096.GSO | SEALING WATER TO 2ND STAGE APPROACH SCREEN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBS203 |  | TM140220HS096 | TM140220EV096 | TM140220EV096 | SEALING WATER TO 2ND STAGE APPROACH SCREEN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBD202 |  | TM140220FS097 | TM140220FS097 | TM140220FS097.L | SEALING WATER TO 2ND STAGE APPROACH SCREEN FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA102 |  | TM140220LC101 | TM140220LT101 | TM140220LT101.MV | WIRE WHITE WATER TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3300 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA102 | TM1402ASD102 | TM140220HC103 | TM140220HV103 | TM140220HV103.OUT | W.W OVERFLOW CHEST PUMP TO SILO CHANNEL CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA102 | TM1402ASD102 | TM140220HC104 | TM140220HV104 | TM140220HV104.OUT | W.W OVERFLOW CHEST PUMP TO W.W COLLECTION TANK CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220XI106 | TM140220XE106 |  | 1ST STAGE APPROACH SCREEN MOTOR VIBRATION 2 | XE | Vibration sensor | Field | [28 empty] | C | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA102 |  | TM140220XI106 | TM140220XT106 | TM140220XT106.MV | 1ST STAGE APPROACH SCREEN MOTOR VIBRATION 2 | XT | Vibration transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | [22 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA202 |  | TM140220PC111 | TM140220PT111 | TM140220PT111.MV | HEADBOX PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA102 | TM1402ASD102 | TM140220HC112 | TM140220HV112 | TM140220HV112.OUT | HEADBOX RECIRCULATION CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140220 |  |  | TM140220FI114 | TM140220FE114 |  | HEADBOX RECIRCULATION FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | B
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM1402JBA102 |  | TM140220FI114 | TM140220FT114 | TM140220FT114.MV | HEADBOX RECIRCULATION FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 5000 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140215 |  |  | TM140215FC005 | TM140215FE005 |  | WET STRENGHT AGENT TO MIXING CHEST PUMP FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3351 | TM140215 | TM1402JBA111 |  | TM140215FC005 | TM140215FT005 | TM140215FT005.MV | WET STRENGHT AGENT TO MIXING CHEST PUMP FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | hold | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140215 |  |  | TM140215FC006 | TM140215FE006 |  | DRY STRENGHT AGENT TO MACHINE CHEST PUMP FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3351 | TM140215 | TM1402JBA111 |  | TM140215FC006 | TM140215FT006 | TM140215FT006.MV | DRY STRENGHT AGENT TO MACHINE CHEST PUMP FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | hold | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140215 |  |  | TM140215FC007 | TM140215FE007 |  | SOFT AGENT TO MIXING CHEST PUMP FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3351 | TM140215 | TM1402JBA111 |  | TM140215FC007 | TM140215FT007 | TM140215FT007.MV | SOFT AGENT TO MIXING CHEST PUMP FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | hold | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140215 |  |  | TM140215FC008 | TM140215FE008 |  | CMC TO FAN PUMP FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3351 | TM140215 | TM1402JBA102 |  | TM140215FC008 | TM140215FT008 | TM140215FT008.MV | CMC TO FAN PUMP FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | hold | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140215 |  |  | TM140215HS069 | TM140215SV069 | TM140215SV069 | WET STRENGHT AGENT TO MIXING CHEST PUMP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3351 | TM140215 | TM1402JBS111 |  | TM140215HS069 | TM140215SV069.ZSC | TM140215SV069.GSC | WET STRENGHT AGENT TO MIXING CHEST PUMP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140215 | TM1402JBS111 |  | TM140215HS069 | TM140215SV069.ZSO | TM140215SV069.GSO | WET STRENGHT AGENT TO MIXING CHEST PUMP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140215 | TM1402JBS111 |  | TM140215HS069 | TM140215EV069 | TM140215EV069 | WET STRENGHT AGENT TO MIXING CHEST PUMP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140215 |  |  | TM140215HS070 | TM140215SV070 | TM140215SV070 | DRY STRENGHT AGENT TO MACHINE CHEST PUMP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3351 | TM140215 | TM1402JBS112 |  | TM140215HS070 | TM140215SV070.ZSC | TM140215SV070.GSC | DRY STRENGHT AGENT TO MACHINE CHEST PUMP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140215 | TM1402JBS112 |  | TM140215HS070 | TM140215SV070.ZSO | TM140215SV070.GSO | DRY STRENGHT AGENT TO MACHINE CHEST PUMP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140215 | TM1402JBS112 |  | TM140215HS070 | TM140215EV070 | TM140215EV070 | DRY STRENGHT AGENT TO MACHINE CHEST PUMP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140215 |  |  | TM140215HS071 | TM140215SV071 | TM140215SV071 | SOFT AGENT TO MIXING CHEST PUMP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3351 | TM140215 | TM1402JBS111 |  | TM140215HS071 | TM140215SV071.ZSC | TM140215SV071.GSC | SOFT AGENT TO MIXING CHEST PUMP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140215 | TM1402JBS111 |  | TM140215HS071 | TM140215SV071.ZSO | TM140215SV071.GSO | SOFT AGENT TO MIXING CHEST PUMP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140215 | TM1402JBS111 |  | TM140215HS071 | TM140215EV071 | TM140215EV071 | SOFT AGENT TO MIXING CHEST PUMP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140215 |  |  | TM140215HS072 | TM140215SV072 | TM140215SV072 | CMC TO FAN PUMP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3351 | TM140215 | TM1402JBS101 |  | TM140215HS072 | TM140215SV072.ZSC | TM140215SV072.GSC | CMC TO FAN PUMP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140215 | TM1402JBS101 |  | TM140215HS072 | TM140215SV072.ZSO | TM140215SV072.GSO | CMC TO FAN PUMP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3351 | TM140215 | TM1402JBS101 |  | TM140215HS072 | TM140215EV072 | TM140215EV072 | CMC TO FAN PUMP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
WHITE WATER AND FIBRE RECOVERY
P-OKITM07-10-320-07-PID-3355 | TM140221 |  |  | TM140221FC001 | TM140221FE001 |  | W.W TO DISC FILTER FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA111 |  | TM140221FC001 | TM140221FT001 | TM140221FT001.MV | W.W TO DISC FILTER FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 5000 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA111 | TM1402ASD112 | TM140221FC001 | TM140221FV001 | TM140221FV001.OUT | W.W TO DISC FILTER FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA101 |  | TM140221LC002 | TM140221LT002 | TM140221LT002.MV | SUPER CLARIFIED TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA101 | TM1402ASD101 | TM140221LC002 | TM140221LV002 | TM140221LV002.OUT | SUPER CLARIFIED TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 |  |  | TM140221FFC003 | TM140221FE003 |  | SWEETENER STOCK FLOW | FE | Magnetic flow Sensor | Field
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA111 |  | TM140221FFC003 | TM140221FT003 | TM140221FT003.MV | SWEETENER STOCK FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1800 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA111 | TM1402ASD112 | TM140221FFC003 | TM140221FV003 | TM140221FV003.OUT | SWEETENER STOCK FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA101 |  | TM140221LC004 | TM140221LT004 | TM140221LT004.MV | CLARIFIED TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA101 | TM1402ASD101 | TM140221LC004 | TM140221LV004 | TM140221LV004.OUT | CLARIFIED TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA101 |  | TM140221LC005 | TM140221LT005 | TM140221LT005.MV | CLOUDY FILTRATE TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3300 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA101 | TM1402ASD101 | TM140221LC005 | TM140221LV005 | TM140221LV005.OUT | CLOUDY FILTRATE TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA101 |  | TM140221LC006 | TM140221LT006 | TM140221LT006.MV | RECOVERED STOCK CHEST LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA111 |  | TM140221LC007 | TM140221LT007 | TM140221LT007.MV | W.W. COLLECTION TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10000 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA111 | TM1402ASD112 | TM140221LC007 | TM140221LV007A | TM140221LV007A.OUT | W.W. COLLECTION TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA111 | TM1402ASD112 | TM140221LC007 | TM140221LV007B | TM140221LV007B.PRO | W.W. COLLECTION TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA101 |  | TM140221PI008 | TM140221PT008 | TM140221PT008.MV | CWW LP SHOWER FILTER INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 |  |  | TM140221PDI009 | TM140221PDX009 | TM140221PDX009.SOF | CWW LP SHOWER FILTER DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function |  |  |  | 0 | 2 | Bar.g | [19 empty] | B
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA101 |  | TM140221PC010 | TM140221PT010 | TM140221PT010.MV | CWW LP SHOWER FILTER FILTER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 |  |  | TM140221HS011 | TM140221SV011 | TM140221SV011 | W.W TO DISC FILTER SHOWERS ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBS201 |  | TM140221HS011 | TM140221SV011.ZSC | TM140221SV011.GSC | W.W TO DISC FILTER SHOWERS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBS201 |  | TM140221HS011 | TM140221SV011.ZSO | TM140221SV011.GSO | W.W TO DISC FILTER SHOWERS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBS201 |  | TM140221HS011 | TM140221EV011 | TM140221EV011 | W.W TO DISC FILTER SHOWERS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | MCC |  | TM140221EI012 | TM140221ET012 | TM140221ET012.MV | DISC FILTER TORQUE | ET | Power transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA201 |  | TM140221PI013 | TM140221PT013 | TM140221PT013.MV | DISC FILTER VACUUM | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBD201 |  | TM140221SS014 | TM140221GS014A | TM140221GS014A.SEC | DISC FILTER SECTOR COUNTER SECTOR PULSE | GS | Proximity Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Sector Pulse | Sector Pulse | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBD201 |  | TM140221SS014 | TM140221GS014B | TM140221GS014B.ROT | DISC FILTER SECTOR COUNTER ROTATION PULSE | GS | Proximity Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Rotation Pulse | Rotation Pulse | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBD201 |  | TM140221SS015 | TM140221SS015 | TM140221SS015.L | DISC FILTER SPEED REPULPER SPEED LOW | SS | Speed Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Speed Low | Not Speed Low | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBD201 |  | TM140221XS016 | TM140221S9 016 | TM140221S9 016.DCS/LOCAL | DISC FILTER LOCAL OPERATION MAINDRIVE DCS/LOCAL | S9 | Selector Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Jog | Jog | [10 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBD201 |  | TM140221XS016 | TM140221S11 016 | TM140221S11 016.JOG | DISC FILTER LOCAL OPERATION MAINDRIVE JOG FORWARD | S11 | Push button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Local | DCS | [10 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBD201 |  | TM140221XS017 | TM140221S9 017 | TM140221S9 017.JOG | DISC FILTER LOCAL OPERATION SHOWER OSCILLATION DCS/LOCAL | S9 | Selector Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Jog | Jog | [10 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBD201 |  | TM140221XS017 | TM140221S11 017 | TM140221S11 017.DCS/LOCAL | DISC FILTER LOCAL OPERATION SHOWER OSCILLATION LOCAL START | S11 | Push button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Local | DCS | [10 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA101 |  | TM140221PI018 | TM140221PT018 | TM140221PT018.MV | SCWW SHOWER FILTER INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 7 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 |  |  | TM140221PDI019 | TM140221PDX019 | TM140221PDX019.SOF | SCWW SHOWER FILTER DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function |  |  |  | 0 | 2 | Bar.g | [19 empty] | B
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA101 |  | TM140221PC020 | TM140221PT020 | TM140221PT020.MV | SCWW SHOWER FILTER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 7 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA201 |  | TM140221LC021 | TM140221LT021 | TM140221LT021.MV | DISC FILTER LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 2000 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA111 |  | TM140221PC022 | TM140221PT022 | TM140221PT022.MV | TM AREA CRC PUMP OUTLET WHITE WATER PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 7 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA101 |  | TM140221PI024 | TM140221PT024 | TM140221PT024.MV | CWW HP SHOWER FILTER FILTER INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 25 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 |  |  | TM140221PDI025 | TM140221PDX025 | TM140221PDX025.SOF | CWW HP SHOWER FILTER DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function |  |  |  | 0 | 2 | Bar.g | [19 empty] | B
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA101 |  | TM140221PC026 | TM140221PT026 | TM140221PT026.MV | CWW HP SHOWER FILTER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 25 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBD201 |  | TM140221XS028 | TM140221S10 028 | TM140221S10 028.ESTOP | DISC FILTER LOCAL OPERATION MAINDRIVE E-STOP | S10 | E - Stop Push Button | +CP01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | E-Stop | [11 empty] | 4 | Andritz
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221CP01 |  | TM140221XS031 | TM140221S1.031 | TM140221S1.031 | CWW LP SHOWER FILTER LOCAL PANEL | S1 | Differential Pressure High alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221CP01 |  | TM140221XS031 | TM140221S2.031 | TM140221S2.031 | CWW LP SHOWER FILTER LOCAL PANEL | S2 | Flush alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221CP01 |  | TM140221XS031 | TM140221S3.031 | TM140221S3.031 | CWW LP SHOWER FILTER LOCAL PANEL | S3 | Power Failure alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221CP02 |  | TM140221XS032 | TM140221S1.032 | TM140221S1.032 | CWW HP SHOWER FILTER LOCAL PANEL | S1 | Differential Pressure High alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221CP02 |  | TM140221XS032 | TM140221S2.032 | TM140221S2.032 | CWW HP SHOWER FILTER LOCAL PANEL | S2 | Flush alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221CP02 |  | TM140221XS032 | TM140221S3.032 | TM140221S3.032 | CWW HP SHOWER FILTER LOCAL PANEL | S3 | Power Failure alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221CP03 |  | TM140221XS033 | TM140221S1.033 | TM140221S1.033 | SCWW SHOWER FILTER LOCAL PANEL | S1 | Differential Pressure High alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221CP03 |  | TM140221XS033 | TM140221S2.033 | TM140221S2.033 | SCWW SHOWER FILTER LOCAL PANEL | S2 | Flush alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221CP03 |  | TM140221XS033 | TM140221S3.033 | TM140221S3.033 | SCWW SHOWER FILTER LOCAL PANEL | S3 | Power Failure alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3355 | TM140221 |  |  | TM140221HS036 | TM140221SV036 | TM140221SV036 | W.W TO DISC FILTER SHOWERS ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBS201 |  | TM140221HS036 | TM140221SV036.ZSC | TM140221SV036.GSC | W.W TO DISC FILTER SHOWERS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBS201 |  | TM140221HS036 | TM140221SV036.ZSO | TM140221SV036.GSO | W.W TO DISC FILTER SHOWERS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBS201 |  | TM140221HS036 | TM140221EV036 | TM140221EV036 | W.W TO DISC FILTER SHOWERS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 |  |  | TM140221FC037 | TM140221FE037 |  | W.W TO DISC FILTER REPULPER FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA201 |  | TM140221FC037 | TM140221FT037 | TM140221FT037.MV | W.W TO DISC FILTER REPULPER FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1000 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA201 | TM1402ASD201 | TM140221FC037 | TM140221FV037 | TM140221FV037.OUT | W.W TO DISC FILTER REPULPER FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA201 |  | TM140221PC038 | TM140221PT038 | TM140221PT038.MV | DISC FILTER SHOWERS PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA101 | TM1402ASD101 | TM140221HC039 | TM140221HV039 | TM140221HV039.OUT | FRESH WATER TO CLOUDY FILTRATE TANK CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBD101 |  | TM140221FS040 | TM140221FS040 | TM140221FS040.L | SEALING WATER TO REC PULP CHEST PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA201 |  | TM140221PI041 | TM140221PT041 | TM140221PT041.MV | W.W TO DISC FILTER SHOWERS PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 |  |  | TM140221HS045 | TM140221SV045 | TM140221SV045 | REC PULP CHEST PUMP OUTLET TO BROKE INTERIM TOWER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBS111 |  | TM140221HS045 | TM140221SV045.ZSC | TM140221SV045.GSC | REC PULP CHEST PUMP OUTLET TO BROKE INTERIM TOWER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBS111 |  | TM140221HS045 | TM140221SV045.ZSO | TM140221SV045.GSO | REC PULP CHEST PUMP OUTLET TO BROKE INTERIM TOWER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBS111 |  | TM140221HS045 | TM140221EV045 | TM140221EV045 | REC PULP CHEST PUMP OUTLET TO BROKE INTERIM TOWER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 |  |  | TM140221HS046 | TM140221SV046 | TM140221SV046 | REC PULP CHEST PUMP OUTLET TO TM 14.2 MIXING CHEST ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBS111 |  | TM140221HS046 | TM140221SV046.ZSC | TM140221SV046.GSC | REC PULP CHEST PUMP OUTLET TO TM 14.2 MIXING CHEST ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBS111 |  | TM140221HS046 | TM140221SV046.ZSO | TM140221SV046.GSO | REC PULP CHEST PUMP OUTLET TO TM 14.2 MIXING CHEST ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBS111 |  | TM140221HS046 | TM140221EV046 | TM140221EV046 | REC PULP CHEST PUMP OUTLET TO TM 14.2 MIXING CHEST ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA101 |  | TM140221PC050 | TM140221PT050 | TM140221PT050.MV | CLOUDY CIRCULATION PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA111 |  | TM140221PC136 | TM140221PT136 | TM140221PT136.MV | YANKEE-TRIM PULPER & OVER FLOW PUMP WHITE WATER PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 |  |  | TM140221HS137 | TM140221SV137 | TM140221SV137 | PULP FROM RECOVERED STOCK CHEST ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBS101 |  | TM140221HS137 | TM140221SV137.ZSC | TM140221SV137.GSC | PULP FROM RECOVERED STOCK CHEST ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBS101 |  | TM140221HS137 | TM140221SV137.ZSO | TM140221SV137.GSO | PULP FROM RECOVERED STOCK CHEST ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBS101 |  | TM140221HS137 | TM140221EV137 | TM140221EV137 | PULP FROM RECOVERED STOCK CHEST ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 |  |  | TM140221NC138 | TM140221NE138 |  | REC PULP CHEST PUMP OUTLET CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230 VAC | [24 empty] | B
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA101 |  | TM140221NC138 | TM140221NT138 | TM140221NT138.MV | REC PULP CHEST PUMP OUTLET CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 6 | %C | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBD101 |  | TM140221NC138 | TM140221NS138 | TM140221NS138.MV | REC PULP CHEST PUMP OUTLET CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA101 | TM1402ASD101 | TM140221NC138 | TM140221NV138 | TM140221NV138.OUT | REC PULP CHEST PUMP OUTLET CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA101 |  | TM140221PC140 | TM140221PT140 | TM140221PT140.MV | PMP DEMAND & CLEANING PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA101 |  | TM140221PC141 | TM140221PT141 | TM140221PT141.MV | SCWW HP SHOWER PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 40 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA111 |  | TM140221FI144 | TM140221FT144 | TM140221FT144.MV | WASTE WATER FROM TM14.2 FLOW | FT | Open channel flow transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 250 | m3/hr | [19 empty] | 4
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM1402JBA101 |  | TM140221PC146 | TM140221PT146 | TM140221PT146.MV | DUST SCWW PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 40 | Bar.g | [19 empty] | 4
VACUUM SYSTEM
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223LC014 | TM140223LT014 | TM110123LT014.MV | VACUUM WW TANK LEVEL | LT | DP Level Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 2500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 | TM1402ASD103 | TM140223LC014 | TM140223LV014 | TM140223LV014.OUT | VACUUM WW TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 | TM1402ASD103 | TM140223HC015 | TM140223HV015 | TM140223HV015.OUT | COOLING TOWER OUTLET BYPASS CV SETPOINT | HV | Control Valve | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBD102 |  | TM140223PS021 | TM140223PS021 | TM140223PS021.L | VACUUM PUMP 1 GEAR REDUCER LUBRICATION OIL PRESSURE | PS | Pressure switch | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBD102 |  | TM140223PS022 | TM140223PS022 | TM140223PS022.L | VACUUM PUMP 2 GEAR REDUCER LUBRICATION OIL PRESSURE | PS | Pressure switch | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223FI065 | TM140223FE065 |  | MAKE-UP WATER VACUUM SYSTEM FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223FI065 | TM140223FT065 | TM140223FT065.MV | MAKE-UP WATER VACUUM SYSTEM FLOW | FT | Magnetic flow transmitter | Field | DCS |  | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 720 | l / min | [19 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223TI066 | TM140223TE066 |  | COOLED SEAL WATER TEMPERATURE | TE | Temperature sensor | Field | [28 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223TI066 | TM140223TT066 | TM140223TT066.MV | COOLED SEAL WATER TEMPERATURE | TT | Temperature transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [19 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223PC067 | TM140223PT067 | TM140223PT067.MV | SEAL WATER TO VACUUM PUMPS PRESSURE | PT | Pressure Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 4 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 | TM1402ASD103 | TM140223PC067 | TM140223PV067 | TM140223PV067.OUT | SEAL WATER TO VACUUM PUMPS PRESSURE CV SETPOINT | PV | Control Valve | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223PI073 | TM140223PT073 | TM140223PT073.MV | VACUUM PUMP 1 PRESSURE | PT | Pressure Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223PI074 | TM140223PT074 | TM140223PT074.MV | VACUUM PUMP 1 PRESSURE | PT | Pressure Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223PI075 | TM140223PT075 | TM140223PT075.MV | VACUUM PUMP 2 PRESSURE | PT | Pressure Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223PI076 | TM140223PT076 | TM140223PT076.MV | VACUUM PUMP 2 PRESSURE | PT | Pressure Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223TI079 | TM140223TE079 |  | COOLING TOWER PUMP 2 OUTLET TEMPERATURE | TE | Temperature sensor | Field | [28 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223TI079 | TM140223TT079 | TM140223TT079.MV | COOLING TOWER PUMP 2 OUTLET TEMPERATURE | TT | Temperature transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [19 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223HS081 | TM140223SV081 | TM140223SV081 | VACUUM PUMP 1 DRAIN ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS081 | TM140223SV081.ZSC | TM140223SV081.GSC | VACUUM PUMP 1 DRAIN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS081 | TM140223SV081.ZSO | TM140223SV081.GSO | VACUUM PUMP 1 DRAIN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS081 | TM140223EV081 | TM140223EV081 | VACUUM PUMP 1 DRAIN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223HS083 | TM140223SV083 | TM140223SV083 | VACUUM PUMP 2 DRAIN ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS083 | TM140223SV083.ZSC | TM140223SV083.GSC | VACUUM PUMP 2 DRAIN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS083 | TM140223SV083.ZSO | TM140223SV083.GSO | VACUUM PUMP 2 DRAIN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS083 | TM140223EV083 | TM140223EV083 | VACUUM PUMP 2 DRAIN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223HS091 | TM140223SV091 | TM140223SV091 | VACUUM PUMP 1 COOLING WATER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS091 | TM140223SV091.ZSC | TM140223SV091.GSC | VACUUM PUMP 1 COOLING WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS091 | TM140223SV091.ZSO | TM140223SV091.GSO | VACUUM PUMP 1 COOLING WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS091 | TM140223EV091 | TM140223EV091 | VACUUM PUMP 1 COOLING WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223FI092 | TM140223FE092 |  | COOLING WATER TO VACUUM PUMP 1 FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223FI092 | TM140223FT092 | TM140223FT092.MV | COOLING WATER TO VACUUM PUMP 1 FLOW | FT | Magnetic flow transmitter | Field | DCS |  | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 430 | l / min | [19 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223HS093 | TM140223SV093 | TM140223SV093 | VACUUM PUMP 2 COOLING WATER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS093 | TM140223SV093.ZSC | TM140223SV093.GSC | VACUUM PUMP 2 COOLING WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS093 | TM140223SV093.ZSO | TM140223SV093.GSO | VACUUM PUMP 2 COOLING WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS093 | TM140223EV093 | TM140223EV093 | VACUUM PUMP 2 COOLING WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223FI094 | TM140223FE094 |  | COOLING WATER TO VACUUM PUMP 2 FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223FI094 | TM140223FT094 | TM140223FT094.MV | COOLING WATER TO VACUUM PUMP 2 FLOW | FT | Magnetic flow transmitter | Field | DCS |  | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 420 | l / min | [19 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223LIS095 | TM140223LT095 | TM140223LT095.MV | VACUUM W.W PIT LEVEL | LT | Radar Level Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | mm |  | 10% | 15% | [16 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 | TM1402ASD103 | TM140223HC096 | TM140223HV096 | TM140223HV096.OUT | COOLING TOWER PUMP OUTLET TO COOLING TOWER CV SETPOINT | HV | Control Valve | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 | TM1402ASD103 | TM140223HC097 | TM140223HV097 | TM140223HV097.OUT | COOLING TOWER PUMP OUTLET TO WIRE WHITE WATER TANK CV SETPOINT | HV | Control Valve | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223HS101 | TM140223SV101 | TM140223SV101 | VACUUM SHEAVE ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS101 | TM140223SV101.ZSC | TM140223SV101.GSC | VACUUM SHEAVE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS101 | TM140223SV101.ZSO | TM140223SV101.GSO | VACUUM SHEAVE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS101 | TM140223EV101 | TM140223EV101 | VACUUM SHEAVE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223PI110 | TM140223PT110 | TM140223PT110.MV | VACUUM PUMP INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 3 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223HC113 | TM140223HV113 | TM140223HV113.OUT | ANTI-SURGE ELECTRIC BUTTERFLY VALVE FEEDBACK | HV | Control Valve | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223HC113 | TM140223HV113 | TM140223HV113.OUT | ANTI-SURGE ELECTRIC BUTTERFLY VALVE CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223LIC114 | TM140223LT114 | TM140223LT114.MV | VACUUM SEPARATOR LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 4
P-OKITM07-10-320-07-PID-3005 | TM140221 | TM1402JBA101 | TM1402ASD103 | TM140223LIC114 | TM140223LV114 | TM140223LV114.OUT | VACUUM SEPARATOR LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223TISA121 | TM140223TE121 |  | FRONT BEARING TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223TISA121 | TM140223TT121 | TM140223TT121.MV | FRONT BEARING TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223TISA122 | TM140223TE122 |  | REAR BEARING TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223TISA122 | TM140223TT122 | TM140223TT122.MV | REAR BEARING TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223TISA123 | TM140223TE123 |  | THRUST BEARING TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223TISA123 | TM140223TT123 | TM140223TT123.MV | THRUST BEARING TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223TISA124 | TM140223TE124 |  | TEMPERATURE OF STATOR WINDING U | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223TISA124 | TM140223TT124 | TM140223TT124.MV | TEMPERATURE OF STATOR WINDING U | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223TISA125 | TM140223TE125 |  | TEMPERATURE OF STATOR WINDING V | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223TISA125 | TM140223TT125 | TM140223TT125.MV | TEMPERATURE OF STATOR WINDING V | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223TISA126 | TM140223TE126 |  | TEMPERATURE OF STATOR WINDING W | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223TISA126 | TM140223TT126 | TM140223TT126.MV | TEMPERATURE OF STATOR WINDING W | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223XISA127 | TM140223XT127 |  | THE OUTPUT SHAFT VIBRATES IN THE X DIRECTION | XT | Vibration sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223XISA127 | TM140223XT127 | TM140223XT127.MV | THE OUTPUT SHAFT VIBRATES IN THE X DIRECTION | XT | Vibration transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | mm | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223XISA128 | TM140223XT128 |  | THE OUTPUT SHAFT VIBRATES IN THE Y DIRECTION | XT | Vibration sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223XISA128 | TM140223XT128 | TM140223XT128.MV | THE OUTPUT SHAFT VIBRATES IN THE Y DIRECTION | XT | Vibration transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | mm | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223TISA131 | TM140223TE131 |  | OIL SUPPLY OIL TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223TISA131 | TM140223TT131 | TM140223TT131.MV | OIL SUPPLY OIL TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223TISA132 | TM140223TE132 |  | TANK OIL TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223TISA132 | TM140223TT132 | TM140223TT132.MV | TANK OIL TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223PC133 | TM140223PT133 | TM140223PT133.MV | OIL SUPPLY PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 16 | Bar.g | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA202 |  | TM140223PC141 | TM140223PT141 | TM140223PT141.MV | UHLE BOX PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 | TM1402ASD103 | TM140123PC141 | TM140123PV141 | TM140123PV141.OUT | UHLE BOX PRESSURE CV SETPOINT | PV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA202 |  | TM140223PI142 | TM140223PT142 | TM140223PT142.MV | PICK-UP BOX PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA202 |  | TM140223PC143 | TM140223PT143 | TM140223PT143.MV | SUCTION PRESS ROLL PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 | TM1402ASD103 | TM140223PC143 | TM140223PV143 | TM140223PV143.OUT | SUCTION PRESS ROLL PRESSURE CV SETPOINT | PV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223HS144 | TM140223SV144 | TM140223SV144 | VACUUM SHEAVE ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS144 | TM140223SV144.ZSC | TM140223SV144.GSC | VACUUM SHEAVE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS144 | TM140223SV144.ZSO | TM140223SV144.GSO | VACUUM SHEAVE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS144 | TM140223EV144 | TM140223EV144 | VACUUM SHEAVE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223HS145 | TM140223SV145 | TM140223SV145 | VACUUM SHEAVE ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS145 | TM140223SV145.ZSC | TM140223SV145.GSC | VACUUM SHEAVE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS145 | TM140223SV145.ZSO | TM140223SV145.GSO | VACUUM SHEAVE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS145 | TM140223EV145 | TM140223EV145 | VACUUM SHEAVE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 |  |  | TM140223HS146 | TM140223SV146 | TM140223SV146 | VACUUM SHEAVE ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS146 | TM140223SV146.ZSC | TM140223SV146.GSC | VACUUM SHEAVE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS146 | TM140223SV146.ZSO | TM140223SV146.GSO | VACUUM SHEAVE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBS102 |  | TM140223HS146 | TM140223EV146 | TM140223EV146 | VACUUM SHEAVE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3353 | TM140223 | TM1402JBA103 |  | TM140223LC147 | TM140223LT147 | TM140223LT147.MV | VACUUM SEPARATOR LEVEL | LT | DP Level Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3000 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 4
| SHOWERS SYSTEM | [37 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-3354 | TM140221 |  |  | TM140221HS095 | TM140221SV095 | TM140221SV095 | WIRE CLEANING (FW2) SHOWER WATER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3354 | TM140221 | TM1402JBS205 |  | TM140221HS095 | TM140221SV095.ZSC | TM140221SV095.GSC | WIRE CLEANING (FW2) SHOWER WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3354 | TM140221 | TM1402JBS205 |  | TM140221HS095 | TM140221SV095.ZSO | TM140221SV095.GSO | WIRE CLEANING (FW2) SHOWER WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3354 | TM140221 | TM1402JBS205 |  | TM140221HS095 | TM140221EV095 | TM140221EV095 | WIRE CLEANING (FW2) SHOWER WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3354 | TM140221 |  |  | TM140221HS096 | TM140221SV096 | TM140221SV096 | SHEET SIDE FELT CLEANING(PW5) SHOWER WATER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3354 | TM140221 | TM1402JBS205 |  | TM140221HS096 | TM140221SV096.ZSC | TM140221SV096.GSC | SHEET SIDE FELT CLEANING(PW5) SHOWER WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3354 | TM140221 | TM1402JBS205 |  | TM140221HS096 | TM140221SV096.ZSO | TM140221SV096.GSO | SHEET SIDE FELT CLEANING(PW5) SHOWER WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3354 | TM140221 | TM1402JBS205 |  | TM140221HS096 | TM140221EV096 | TM140221EV096 | SHEET SIDE FELT CLEANING(PW5) SHOWER WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3354 | TM140221 |  |  | TM140221HS097 | TM140221SV097 | TM140221SV097 | FLOODED NIP (PW7) SHOWER WATER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 0
P-OKITM07-10-320-07-PID-3354 | TM140221 | TM1402JBS205 |  | TM140221HS097 | TM140221SV097.ZSC | TM140221SV097.GSC | FLOODED NIP (PW7) SHOWER WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3354 | TM140221 | TM1402JBS205 |  | TM140221HS097 | TM140221SV097.ZSO | TM140221SV097.GSO | FLOODED NIP (PW7) SHOWER WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3354 | TM140221 | TM1402JBS205 |  | TM140221HS097 | TM140221EV097 | TM140221EV097 | FLOODED NIP (PW7) SHOWER WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3354 | TM140221 |  |  | TM140221HS098 | TM140221SV098 | TM140221SV098 | TAIL CUTTER (PW3) SHOWER WATER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 0
P-OKITM07-10-320-07-PID-3354 | TM140221 | TM1402JBS205 |  | TM140221HS098 | TM140221SV098.ZSC | TM140221SV098.GSC | TAIL CUTTER (PW3) SHOWER WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3354 | TM140221 | TM1402JBS205 |  | TM140221HS098 | TM140221SV098.ZSO | TM140221SV098.GSO | TAIL CUTTER (PW3) SHOWER WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3354 | TM140221 | TM1402JBS205 |  | TM140221HS098 | TM140221EV098 | TM140221EV098 | TAIL CUTTER (PW3) SHOWER WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
FRESH WATER
P-OKITM07-10-320-07-PID-3009 | TM140222 | TM1402JBA102 |  | TM140222LC002 | TM140222LT002 | TM140222LT002.MV | WARM WATER TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3300 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3009 | TM140222 | TM1402JBA102 | TM1402ASD102 | TM140222LC002 | TM140222LV002 | TM140222LV002.OUT | WARM WATER TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3009 | TM140222 |  |  | TM140222TC004 | TM140222TE004 |  | WARM WATER TANK TEMPERATURE TEMPERATURE | TE | Temperature Sensor | Field
P-OKITM07-10-320-07-PID-3009 | TM140222 | TM1402JBA102 |  | TM140222TC004 | TM140222TT004 | TM140222TT004.MV | WARM WATER TANK TEMPERATURE TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [19 empty] | 1
P-OKITM07-10-320-07-PID-3009 | TM140222 | TM1402JBA102 | TM1402ASD102 | TM140222TC004 | TM140222TV004 | TM140222TV004.OUT | WARM WATER TANK TEMPERATURE TEMPERATURE CV SETPOINT | TV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3009 | TM140222 | TM1402JBA102 |  | TM140222PC008 | TM140222PT008 | TM140222PT008.MV | FELT HP SHOWER PUMP 1 OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 7 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3009 | TM140222 | TM1402JBA102 |  | TM140222PC009 | TM140222PT009 | TM140222PT009.MV | FELT HP SHOWER PUMP 2 OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 40 | Bar.g | [19 empty] | 1
COMPRESSED AIR
P-OKITM07-10-320-07-PID-3358 | TM140201 | TM1402JBA112 |  | TM140201PI002 | TM140201PT002 | TM140201PT002.MV | MILL COMPRESSED AIR PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3358 | TM140201 |  |  | TM140201HS003 | TM140201SV003 | TM140201SV003 | COMPRESSED AIR TO TM14.2 ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-3358 | TM140201 | TM1402JBS112 |  | TM140201HS003 | TM140201SV003.ZSC | TM140201SV003.GSC | COMPRESSED AIR TO TM14.2 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3358 | TM140201 | TM1402JBS112 |  | TM140201HS003 | TM140201SV003.ZSO | TM140201SV003.GSO | COMPRESSED AIR TO TM14.2 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3358 | TM140201 | TM1402JBS112 |  | TM140201HS003 | TM140201EV003 | TM140201EV003 | COMPRESSED AIR TO TM14.2 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3358 | TM140201 | TM1402JBA112 |  | TM140201PI004 | TM140201PT004 | TM140201PT004.MV | INSTRUMENT AIR STORAGE TANK #1 PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3358 | TM140201 |  |  | TM140201HS005 | TM140201SV005 | TM140201SV005 | INSTRUMENT AIR STORAGE TANK #1 DRAIN ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-3358 | TM140201 | TM1402JBS112 |  | TM140201HS005 | TM140201SV005.ZSC | TM140201SV005.GSC | INSTRUMENT AIR STORAGE TANK #1 DRAIN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3358 | TM140201 | TM1402JBS112 |  | TM140201HS005 | TM140201SV005.ZSO | TM140201SV005.GSO | INSTRUMENT AIR STORAGE TANK #1 DRAIN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3358 | TM140201 | TM1402JBS112 |  | TM140201HS005 | TM140201EV005 | TM140201EV005 | INSTRUMENT AIR STORAGE TANK #1 DRAIN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
NaOH SYSTEM
P-OKITM07-10-320-07-PID-3010 | TM140215 |  |  | TM140215HS013 | TM140215SV013 | TM140215SV013 | 32% NaOH TO TM14.2 ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3010 | TM140215 | TM1402JBS205 |  | TM140215HS013 | TM140215SV013.ZSC | TM140215SV013.GSC | 32% NaOH TO TM14.2 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3010 | TM140215 | TM1402JBS205 |  | TM140215HS013 | TM140215SV013.ZSO | TM140215SV013.GSO | 32% NaOH TO TM14.2 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3010 | TM140215 | TM1402JBS205 |  | TM140215HS013 | TM140215EV013 | TM140215EV013 | 32% NaOH TO TM14.2 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
YANKEE COATING
P-OKITM07-10-320-07-PID-3357 | TM140216 | Supplier JB |  | TM140216FC001 | TM140216FE001 |  | RELEASE AGENT PUMP 1 OUTLET FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3357 | TM140216 | Supplier JB |  | TM140216FC001 | TM140216FT001 | TM140216FT001.MV | RELEASE AGENT PUMP 1 OUTLET FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR |  |  | l / min | [19 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3357 | TM140216 | Supplier JB |  | TM140216FI003 | TM140216FE003 |  | RELEASE AGENT PUMP 2 OUTLET FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3357 | TM140216 | Supplier JB |  | TM140216FI003 | TM140216FT003 | TM140216FT003.MV | RELEASE AGENT PUMP 2 OUTLET FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR |  |  | l / min | [19 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3357 | TM140216 | Supplier JB |  | TM140216FI005 | TM140216FE005 |  | RELEASE AGENT PUMP 3 OUTLET FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3357 | TM140216 | Supplier JB |  | TM140216FI005 | TM140216FT005 | TM140216FT005.MV | RELEASE AGENT PUMP 3 OUTLET FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR |  |  | l / min | [19 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3357 | TM140216 | Supplier JB |  | TM140216PC007 | TM140216PT007 | TM140216PT007.MV | YANKEE COATING PUMP 1&2 OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 |  | Bar.g | [19 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3357 | TM140216 | Supplier JB |  | TM140216FI010 | TM140216FE010 |  | YANKEE COATING PUMP 1&2 OUTLET FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3357 | TM140216 | Supplier JB |  | TM140216FI010 | TM140216FT010 | TM140216FT010.MV | YANKEE COATING PUMP 1&2 OUTLET FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR |  |  | l / min | [19 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3357 | TM140216 | Supplier JB |  | TM140216LI021 | TM140216LI021 | TM140216LI021.MV | COATING TANK LEVEL | LI | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 |  | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 3 |  | HOLD,not finalised
P-OKITM07-10-320-07-PID-3357 | TM140216 | Supplier JB |  | TM140216LI022 | TM140216LI022 | TM140216LI022.MV | RELEASE TANK LEVEL | LI | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 |  | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 3 |  | HOLD,not finalised
P-OKITM07-10-320-07-PID-3357 | TM140216 | Supplier JB |  | TM140216LI023 | TM140216LI023 | TM140216LI023.MV | MAP TANK LEVEL | LI | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 |  | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 3 |  | HOLD,not finalised
STEAM AND CONDENSATE SYSTEM
P-OKITM07-10-320-07-PID-3006 | TM140235 |  |  | TM140235TI001 | TM140235TE001 |  | TO YANKEE 13.5BAR STEAM TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 3 | PMP | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140235 | TM1402JBA112 |  | TM140235TI001 | TM140235TT001 | TM140235TT001.MV | TO YANKEE 13.5BAR STEAM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 350 | ˚C | [19 empty] | 3 | PMP | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140235 | TM1402JBA112 |  | TM140235PI002 | TM140235PT002 | TM140235PT002.MV | TO YANKEE 13.5BAR STEAM PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 15 | Bar.g | [19 empty] | 3 | PMP | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140235 | TM1402JBA112 |  | TM140235FI003 | TM140235FT003 | TM140235FT003.MV | TO YANKEE 13.5BAR STEAM FLOW | FT | Vortex Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 11 | t/h | [19 empty] | 3 | PMP | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140235 |  |  | TM140235TI015 | TM140235TE015 |  | TO YANKEE 20BAR STEAM TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 3 |  | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140235 | TM1402JBA112 |  | TM140235TI015 | TM140235TT015 | TM140235TT015.MV | TO YANKEE 20BAR STEAM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 3 |  | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140235 | TM1402JBA112 |  | TM140235PI016 | TM140235PT016 | TM140235PT016.MV | TO YANKEE 20BAR STEAM PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 25 | Bar.g | [19 empty] | 3 |  | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140235 | TM1402JBA112 |  | TM140235FI017 | TM140235FT017 | TM140235FT017.MV | TO YANKEE 20BAR STEAM FLOW | FT | Vortex Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6.5 | t/h | [19 empty] | 3 |  | Already In PMP IO List
Hall ventilation
P-OKITM07-10-320-08-FLD-3001 | TM140200 | TM1402JBD202 |  | TM140200PDS102 | TM140200PDS102 | TM140200PDS102.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 1
P-OKITM07-10-320-08-FLD-3001 | TM140200 | TM1402JBD202 |  | TM140200PDS103 | TM140200PDS103 | TM140200PDS103.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 1
P-OKITM07-10-320-08-FLD-3001 | TM140200 | TM1402JBD301 |  | TM140200PDS104 | TM140200PDS104 | TM140200PDS104.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 1
P-OKITM07-10-320-08-FLD-3001 | TM140200 | TM1402JBD301 |  | TM140200PDS105 | TM140200PDS105 | TM140200PDS105.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 1
P-OKITM07-10-320-08-FLD-3001 | TM140200 | TM1402JBD301 |  | TM140200PDS106 | TM140200PDS106 | TM140200PDS106.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 1
P-OKITM07-10-320-08-FLD-3001 | TM140200 | TM1402JBD301 |  | TM140200XS107 | TM140200XS107 | TM140200XS107 | TM 14.2 EXHAUST AIR FAN1 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3001 | TM140200 | TM1402JBD301 |  | TM140200XS108 | TM140200XS108 | TM140200XS108 | TM 14.2 EXHAUST AIR FAN2 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3001 | TM140200 | TM1402JBD301 |  | TM140200XS109 | TM140200XS109 | TM140200XS109 | TM 14.2 EXHAUST AIR FAN3 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3001 | TM140200 | TM1402JBD301 |  | TM140200XS110 | TM140200XS110 | TM140200XS110 | TM 14.2 EXHAUST AIR FAN4 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3001 | TM140200 | TM1402JBD301 |  | TM140200XS111 | TM140200XS111 | TM140200XS111 | TM 14.2 EXHAUST AIR FAN5 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3001 | TM140200 | TM1402JBD301 |  | TM140200XS112 | TM140200XS112 | TM140200XS112 | TM 14.2 EXHAUST AIR FAN6 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
HVAC Air Condition
P-OKITM07-10-320-08-FLD-3351 | TM140200 | NA |  | TM140200PDS001 | TM140200PDS001 | TM140200PDS001.L | TM 14.2 TM MCC ROOM AIR FAN FILTER 1 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3351 | TM140200 | NA |  | TM140200PDS002 | TM140200PDS002 | TM140200PDS002.L | TM 14.2 TM MCC ROOM AIR FAN FILTER 2 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3351 | TM140200 | NA |  | TM140200PDS003 | TM140200PDS003 | TM140200PDS003.L | TM 14.2 TM MCC ROOM AIR FAN FILTER 3 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3351 | TM140200 | NA |  | TM140200PDS004 | TM140200PDS004 | TM140200PDS004.L | TM 14.2 TM MCC ROOM AIR FAN FILTER 4 DIFFERENTIAL PRESSURE(MAU1) | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3351 | TM140200 | NA |  | TM140200PDS005 | TM140200PDS005 | TM140200PDS005.L | TM 14.2 TM MCC ROOM AIR FAN FILTER 4 DIFFERENTIAL PRESSURE(MAU2) | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3351 | TM140200 | NA |  | TM140200XS006 | TM140200XS006 | TM140200XS006 | TM 14.2 TM MCC ROOM AC1 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3351 | TM140200 | NA |  | TM140200XS007 | TM140200XS007 | TM140200XS007 | TM 14.2 TM MCC ROOM AC2 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3351 | TM140200 | NA |  | TM140200XS008 | TM140200XS008 | TM140200XS008 | TM 14.2 TM MCC ROOM AC3 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3351 | TM140200 | NA |  | TM140200XS009 | TM140200XS009 | TM140200XS009 | TM 14.2 TM MCC ROOM AC4 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3351 | TM140200 | NA |  | TM140200II010 | TM140200IT010 | TM140200IT010.MV | TM 14.2 TM MCC ROOM AC PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3351 | TM140200 | NA |  | TM140200II011 | TM140200IT011 | TM140200IT011.MV | TM 14.2 SUPPLY FAN PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3351 | TM140200 | NA |  | TM140200II012 | TM140200IT012 | TM140200IT012.MV | TM 14.2 EXHAUST FAN PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3351 | TM140200 | NA |  | TM140200TI013 | TM140200TT013 | TM140200TT013.MV | TM 14.2 TM MCC ROOM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 0 | 50 | ˚C
P-OKITM07-10-320-08-FLD-3351 | TM140200 | NA |  | TM140200MI014 | TM140200MT014 | TM140200MT014.MV | TM 14.2 TM MCC ROOM HUMIDITY | MT | Humidity Transmitter(Integrated In TT) | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 40 | 60 | %
P-OKITM07-10-320-08-FLD-3351 | TM140200 | NA |  | TM140200TI015 | TM140200TT015 | TM140200TT015.MV | TM 14.2 TM RACK ROOM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 0 | 50 | ˚C
P-OKITM07-10-320-08-FLD-3351 | TM140200 | NA |  | TM140200MI016 | TM140200MT016 | TM140200MT016.MV | TM 14.2 TM RACK ROOM HUMIDITY | MT | Humidity Transmitter(Integrated In TT) | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 40 | 60 | %

## 14.2 Exchange Communication lst
PMT: |  |  |  |  | Design Institute: |  |  | Project No. | P-OKITM07-10 | [6 empty] | EXCHANGE COMMUNICTION LIST
[8 empty] | Project Name | DETAIL ENGINEERING FOR 4(FOUR) UNITS TISSUE MACHINE
[8 empty] | Doc. No. | P-OKITM07-10-320-06-LST-3355 | [7 empty] | Abbreviations
Owner: | [7 empty] | Rev. No. | 4 |  |  | Prep'd by | Dengzuijie |  |  |  | EER Electronic Equipment Room |  |  |  | SQRT Square Root
[8 empty] | Purpose | Final |  |  | Chk'd by | Chengjianguo |  |  |  | CCR Control Center Room
[8 empty] | Date | 8,30,2021 |  |  | Appv'd by | LiXiangdong |  |  |  | ESP Electrostatic Precipitator
P&ID No. | Area | Motor Tag reference | Loop No. | Tag No. | System Tag No. | Service Description | Signal Tag | Instrument Type | Location | System | IO Type | Signal |  |  | IO Loc. | PV LO | PV HI | Eng. Unit | Alarm | [6 empty] | State "0" | State "1" | CV Fail Action | CV Ctrl Action | PV CHAR | From |  | Cable |  |  | To |  | Rev. | Supply | Remarks
[12 empty] | Type | Power | Wire |  |  |  |  | LLL | LL | L | Nor. | H | HH | HHH | [5 empty] | JB/Panel No. | TB | Cable Number | Cable Type | Cable Order | Cabinet No. | TB |  | By
MACHINE BROKE
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM140217U003 | TM140217SC025 | TM140217SX025 | TM140217SX025.PRO | BROKE INTERIM TOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM140217U001 | TM140217SC050 | TM140217SX050 | TM140217SX050.PRO | BROKE DEFLAKED CHEST PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM140217A004 | TM140217SC054 | TM140217SX054 | TM140217SX054.PRO | YANKEE PULPER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 2
P-OKITM07-10-320-07-PID-3352 | TM140217 | TM140217U002 | TM140217SC092 | TM140217SX092 | TM140217SX092.PRO | BROKE THICKENER TANK PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
STOCK APPROACH
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220U001 | TM140220SC013 | TM140220SX013 | TM140220SX013.PRO | MIXING CHEST PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220M001 | TM140220EC033 | TM140220SX013 | TM140220SX013.PRO | TICKLER REFINER POWER VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220U003 | TM140220SC046 | TM140220SX046 | TM140220SX046.PRO | SWEETENER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220U004 | TM140220SC056 | TM140220SX056 | TM140220SX056.PRO | MACHINE CHEST PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220U006 | TM140220SC071 | TM140220SX071 | TM140220SX071.PRO | FAN PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3351 | TM140220 | TM140220U007 | TM140220SC102 | TM140220SX102 | TM140220SX102.PRO | W.W OVERFLOW CHEST PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3351 | TM140215 |  | TM140215FC005 | TM140215FX005A | TM140215FX005A.PRO | WET STRENGHT AGENT TO MIXING CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3351 | TM140215 |  | TM140215FC005 | TM140215FX005B | TM140215FX005B.PRO | WET STRENGHT AGENT TO MIXING CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3351 | TM140215 |  | TM140215FC006 | TM140215FX006A | TM140215FX006A.PRO | DRY STRENGHT AGENT TO MACHINE CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3351 | TM140215 |  | TM140215FC006 | TM140215FX006B | TM140215FX006B.PRO | DRY STRENGHT AGENT TO MACHINE CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3351 | TM140215 |  | TM140215FC007 | TM140215FX007A | TM140215FX007A.PRO | SOFT AGENT TO MIXING CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3351 | TM140215 |  | TM140215FC007 | TM140215FX007B | TM140215FX007B.PRO | SOFT AGENT TO MIXING CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3351 | TM140215 |  | TM140215FC008 | TM140215FX008A | TM140215FX008A.PRO | CMC TO FAN PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3351 | TM140215 |  | TM140215FC008 | TM140215FX008B | TM140215FX008B.PRO | CMC TO FAN PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
WHITE WATER AND FIBRE RECOVERY
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221M001 | TM140221SC027 | TM140221SX027 | TM140221SX027.PRO | DISC FILTER MOTOR SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221U001 | TM140221SC029 | TM140221SX029 | TM140221SX029.PRO | DISC FILTER FEED PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221U002 | TM140221SC030 | TM140221SX030 | TM140221SX030.PRO | TM AREA CRC PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221U003 | TM140221SC031 | TM140221SX031 | TM140221SX031.PRO | YANKEE-TRIM PULPER & OVER FLOW PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221U007 | TM140221SC032 | TM140221SX032 | TM140221SX032.PRO | CLARIFIED TANK PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221U008 | TM140221SC033 | TM140221SX033 | TM140221SX033.PRO | DISC FILTER SHOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221U004 | TM140221SC047 | TM140221SX047 | TM140221SX047.PRO | REC PULP CHEST PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221U009 | TM140221SC048 | TM140221SX048 | TM140221SX048.PRO | CWW LP SHOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221U006 | TM140221SC049 | TM140221SX049 | TM140221SX049.PRO | CWW HP SHOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221U005 | TM140221SC051 | TM140221SX051 | TM140221SX051.PRO | CLOUDY CIRCULATION PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221U011 | TM140221SC052 | TM140221SX052 | TM140221SX052.PRO | SCWW LP SHOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221U013 | TM140221SC142 | TM140221SX142 | TM140221SX142.PRO | SCWW HP SHOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3355 | TM140221 | TM140221U012 | TM140221SC143 | TM140221SX143 | TM140221SX143.PRO | PMP DEMAND & CLEANING PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3355 | TM140121 | TM140221U014 | TM140121SC146 | TM140121SX146 | TM140121SX146.PRO | DUST SCWW PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
FRESH WATER
P-OKITM07-10-320-07-PID-3009 | TM140222 | TM140222U008 | TM140222SC031 | TM140222SX031 | TM140222SX031.PRO | WARM WATER PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3009 | TM140222 | TM140222U009 | TM140222SC032 | TM140222SX032 | TM140222SX032.PRO | WARM WATER PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3009 | TM140222 | TM140222U010 | TM140222SC033 | TM140222SX033 | TM140222SX033.PRO | FELT HP SHOWER PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3009 | TM140222 | TM140222U011 | TM140222SC034 | TM140222SX034 | TM140222SX034.PRO | FELT HP SHOWER PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
YANKEE COATING
P-OKITM07-10-320-07-PID-3357 | TM140216 |  | TM140216SC002 | TM140216SX002 | TM140216SX002.PRO | RELEASE AGENT PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3357 | TM140216 |  | TM140216SC004 | TM140216SX004 | TM140216SX004.PRO | RELEASE AGENT PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3357 | TM140216 |  | TM140216SC006 | TM140216SX006 | TM140216SX006.PRO | RELEASE AGENT PUMP 3 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3357 | TM140216 |  | TM140216SC008 | TM140216SX008 | TM140216SX008.PRO | YANKEE COATING PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3357 | TM140216 |  | TM140216SC009 | TM140216SX009 | TM140216SX009.PRO | YANKEE COATING PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B

## IO Summary
I/O COUNT SUMMARY
| AI | AO | DI | DO | TOTAL | REMARK
DCS | 118 | 45 | 195 | 78 | 436
SIS | 0 | 0 | 0 | 0 | 0
SUM | 118 | 45 | 195 | 78 | 436

## Definitions
P&ID No. | The P&ID drawing number where the equipment is located.
Area | The Area where the equipment is located
Loop No. | Loop Number
Tag No. | Tag Name according to APP guideline
System Tag No. | Tag name to be appeared in DCS
Service Description | Process/service description
Signal Tag | Signal Tagname
Instrument Type | Type of instrument
Location | Location of the instrument
System | in DCS, PLC or local
IO Type | Type of input or output
Signal - Type | Signal type
Signal - Power | Power for the signal
Signal - Wire | wiring configuration
IO Loc. | Input and Output location
PV LO | Range Low
PV HI | Range High
Eng. Unit | Engineering Unit
Alarm | LLL- Low Low Low, HHH- High High High etc
State "0" | For Valves, If signal is zero, what willl be the valve opening.
State "1" | For Valves, If signal is one, what willl be the valve opening.
CV fail Action | For Valves, If air fails, what willl be the valve status.
CV Control Action | For Valves, Direction of the control.
PV CHAR | Process value characteristics
Rev | Revision
Supply By | Supplier name
Remarks