## 14.3-IO Database
PMT: | [5 empty] | Design Institute: |  |  | Project No. | P-OKITM07-10 | [6 empty] | DCS I/O Database
[9 empty] | Project Name | DETAIL ENGINEERING FOR 4(FOUR) UNITS TISSUE MACHINE
[9 empty] | Doc. No. | P-OKITM07-10-320-06-LST-3705 | [7 empty] | Abbreviations
Owner: | [8 empty] | Rev. No. | 4 |  |  | Prep'd by | Dengzuijie |  |  |  | EER Electronic Equipment Room |  |  |  | SQRT Square Root
[9 empty] | Purpose | Final |  |  | Chk'd by | Chengjianguo |  |  |  | CCR Control Center Room
[9 empty] | Date | 8,30,2021 |  |  | Appv'd by | LiXiangdong |  |  |  | ESP Electrostatic Precipitator
P&ID No. | Area | JB No. | ASD No. | Loop No. | Tag No. | System Tag No. | Service Description | Signal Tag | Instrument Type | Location | System | IO Type | Signal |  |  | IO Loc. | PV LO | PV HI | Eng. Unit | Alarm | [6 empty] | State "0" | State "1" | CV Fail Action | CV Ctrl Action | PV CHAR | From |  | Cable |  |  | To |  | Rev. | Supply | Remarks
[13 empty] | Type | Power | Wire |  |  |  |  | LLL | LL | L | Nor. | H | HH | HHH | [5 empty] | JB/Panel No. | TB | Cable Number | Cable Type | Cable Order | Cabinet No. | TB |  | By
MACHINE BROKE
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD102 |  | TM140317FS001 | TM140317FS001 | TM140317FS001.L | SEALING WATER TO YANKEE PULPER PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD111 |  | TM140317FS002 | TM140317FS002 | TM140317FS002.L | SEALING WATER TO BROKE DEFLAKED CHEST PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD111 |  | TM140317FS003 | TM140317FS003 | TM140317FS003.L | SEALING WATER TO BROKE INTERIM TOWER PUMP 2 FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS005 | TM140317SV005 | TM140317SV005 | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS103 |  | TM140317HS005 | TM140317SV005.ZSC | TM140317SV005.GSC | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS103 |  | TM140317HS005 | TM140317SV005.ZSO | TM140317SV005.GSO | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS103 |  | TM140317HS005 | TM140317EV005 | TM140317EV005 | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS006 | TM140317SV006 | TM140317SV006 | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS103 |  | TM140317HS006 | TM140317SV006.ZSC | TM140317SV006.GSC | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS103 |  | TM140317HS006 | TM140317SV006.ZSO | TM140317SV006.GSO | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS103 |  | TM140317HS006 | TM140317EV006 | TM140317EV006 | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA103 |  | TM140317LC007 | TM140317LT007 | TM140317LT007.MV | YANKEE PULPER LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 5000 | mm |  | 20% | 30% |  | 80% | 90% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA103 | TM1403ASD104 | TM140317LC007 | TM140317LV007A | TM140317LV007A.OUT | YANKEE PULPER LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA103 | TM1403ASD104 | TM140317LC007 | TM140317LV007B | TM140317LV007B.OUT | YANKEE PULPER LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA103 | TM1403ASD104 | TM140317LC007 | TM140317LV007C | TM140317LV007C.OUT | YANKEE PULPER LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317EC008 | TM140317EX008 | TM140317EX008.SOF | YANKEE PULPER SHEET BREAK | EX | DCS software function | DCS | DCS |  | Software function | [25 empty] | B
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD102 |  | TM140317FS009 | TM140317FS009 | TM140317FS009.L | SEALING WATER TO YANKEE PULPER RECIRCULATION PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD102 |  | TM140317FS010 | TM140317FS010 | TM140317FS010.L | SEALING WATER TO YANKEE PULPER AGITATOR FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS011 | TM140317SV011 | TM140317SV011 | YANKEE PULPER SHOWER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS103 |  | TM140317HS011 | TM140317SV011.ZSC | TM140317SV011.GSC | YANKEE PULPER SHOWER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS103 |  | TM140317HS011 | TM140317SV011.ZSO | TM140317SV011.GSO | YANKEE PULPER SHOWER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS103 |  | TM140317HS011 | TM140317EV011 | TM140317EV011 | YANKEE PULPER SHOWER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317NC012 | TM140317NE012 |  | PULP FROM YANKEE PULPER TO BROKE INTERIM TOWER CONSISTENCY | NE | Blade Consistency Sensor | Field | [28 empty] | 0
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA103 |  | TM140317NC012 | TM140317NT012 | TM140317NT012.MV | PULP FROM YANKEE PULPER TO BROKE INTERIM TOWER CONSISTENCY | NT | Blade Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 6 | %Cs | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317FC113 | TM140317FE113 |  | DILUTITION WATER TO YANKEE PULPER FLOW | FE | Magnetic Flow Sensor | Field | DCS | [27 empty] | B
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA103 |  | TM140317FC113 | TM140317FT113 | TM140317FT113.MV | DILUTITION WATER TO YANKEE PULPER FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 3500 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA103 | TM1403ASD104 | TM140317FC113 | TM140317FV113 | TM140317FV113.OUT | DILUTITION WATER TO YANKEE PULPER FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA112 |  | TM140317LI015 | TM140317LT015 | TM140317LT015.MV | BROKE INTERIM TOWER LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 12600 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS016 | TM140317SV016 | TM140317SV016 | PULP FROM BROKE INTERIM TOWER TO BROKE INTERIM TOWER PUMP 2 ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS113 |  | TM140317HS016 | TM140317SV016.ZSC | TM140317SV016.GSC | PULP FROM BROKE INTERIM TOWER TO BROKE INTERIM TOWER PUMP 2 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS113 |  | TM140317HS016 | TM140317SV016.ZSO | TM140317SV016.GSO | PULP FROM BROKE INTERIM TOWER TO BROKE INTERIM TOWER PUMP 2 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS113 |  | TM140317HS016 | TM140317EV016 | TM140317EV016 | PULP FROM BROKE INTERIM TOWER TO BROKE INTERIM TOWER PUMP 2 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA112 | TM1404ASD113 | TM140317HC017 | TM140317HV017 | TM140317HV017.OUT | BROKE INTERIM TOWER PUMP 1 INLET DILUTION WATER CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS020 | TM140317SV020 | TM140317SV020 | PULP FROM BROKE INTERIM TOWER TO PUMP 1 ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS113 |  | TM140317HS020 | TM140317SV020.ZSC | TM140317SV020.GSC | PULP FROM BROKE INTERIM TOWER TO PUMP 1 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS113 |  | TM140317HS020 | TM140317SV020.ZSO | TM140317SV020.GSO | PULP FROM BROKE INTERIM TOWER TO PUMP 1 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS113 |  | TM140317HS020 | TM140317EV020 | TM140317EV020 | PULP FROM BROKE INTERIM TOWER TO PUMP 1 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS021 | TM140317SV021 | TM140317SV021 | HC-CLEANER FEED ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS201 |  | TM140317HS021 | TM140317SV021.ZSC | TM140317SV021.GSC | HC-CLEANER FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS201 |  | TM140317HS021 | TM140317SV021.ZSO | TM140317SV021.GSO | HC-CLEANER FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS201 |  | TM140317HS021 | TM140317EV021 | TM140317EV021 | HC-CLEANER FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS022 | TM140317SV022 | TM140317SV022 | HC-CLEANER ACCEPT ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS201 |  | TM140317HS022 | TM140317SV022.ZSC | TM140317SV022.GSC | HC-CLEANER ACCEPT ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS201 |  | TM140317HS022 | TM140317SV022.ZSO | TM140317SV022.GSO | HC-CLEANER ACCEPT ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS201 |  | TM140317HS022 | TM140317EV022 | TM140317EV022 | HC-CLEANER ACCEPT ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS023 | TM140317SV023 | TM140317SV023 | HC-CLEANER BYPASS ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS201 |  | TM140317HS023 | TM140317SV023.ZSC | TM140317SV023.GSC | HC-CLEANER BYPASS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS201 |  | TM140317HS023 | TM140317SV023.ZSO | TM140317SV023.GSO | HC-CLEANER BYPASS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS201 |  | TM140317HS023 | TM140317EV023 | TM140317EV023 | HC-CLEANER BYPASS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA201 |  | TM140317PC028 | TM140317PT028 | TM140317PT028.MV | HC-CLEANER FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA201 |  | TM140317PC029 | TM140317PT029 | TM140317PT029.MV | HC-CLEANER ACCEPT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA201 | TM1403ASD201 | TM140317PC029 | TM140317PV029 | TM140317PV029.OUT | HC-CLEANER ACCEPT PRESSURE CV SETPOINT | PV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317KS031 | TM140317KX031 | TM140317KX031.SOF | HC-CLEANER JUNK TRAP SEQUENCE | KX | DCS software function | DCS | DCS |  | Software function
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS031A | TM140317SV031A | TM140317SV031A | HC-CLEANER REJECT TOP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD203 |  | TM140317HS031A | TM140317SV031A.ZSC | TM140317SV031A.GSC | HC-CLEANER REJECT TOP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD203 |  | TM140317HS031A | TM140317SV031A.ZSO | TM140317SV031A.GSO | HC-CLEANER REJECT TOP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD203 | TM1403ASD202 | TM140317HS031A | TM140317EV031A | TM140317EV031A | HC-CLEANER REJECT TOP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS031B | TM140317SV031B | TM140317SV031B | HC-CLEANER REJECT BOTTOM ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD203 |  | TM140317HS031B | TM140317SV031B.ZSC | TM140317SV031B.GSC | HC-CLEANER REJECT BOTTOM ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD203 |  | TM140317HS031B | TM140317SV031B.ZSO | TM140317SV031B.GSO | HC-CLEANER REJECT BOTTOM ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD203 | TM1403ASD202 | TM140317HS031B | TM140317EV031B | TM140317EV031B | HC-CLEANER REJECT BOTTOM ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS031C | TM140317SV031C | TM140317SV031C | HC-CLEANER REJECT TOP FLUSHING ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD203 |  | TM140317HS031C | TM140317SV031C.ZSC | TM140317SV031C.GSC | HC-CLEANER REJECT TOP FLUSHING ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD203 |  | TM140317HS031C | TM140317SV031C.ZSO | TM140317SV031C.GSO | HC-CLEANER REJECT TOP FLUSHING ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD203 | TM1403ASD202 | TM140317HS031C | TM140317EV031C | TM140317EV031C | HC-CLEANER REJECT TOP FLUSHING ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS031D | TM140317SV031D | TM140317SV031D | HC-CLEANER REJECT BOTTOM FLUSHING ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD203 |  | TM140317HS031D | TM140317SV031D.ZSC | TM140317SV031D.GSC | HC-CLEANER REJECT BOTTOM FLUSHING ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD203 |  | TM140317HS031D | TM140317SV031D.ZSO | TM140317SV031D.GSO | HC-CLEANER REJECT BOTTOM FLUSHING ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD203 | TM1403ASD202 | TM140317HS031D | TM140317EV031D | TM140317EV031D | HC-CLEANER REJECT BOTTOM FLUSHING ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS031E | TM140317SV031E | TM140317SV031E | HC-CLEANER REJECT EXHAUSTING ON/OFF VALVE OPENED | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD203 |  | TM140317HS031E | TM140317SV031E.ZSC | TM140317SV031E.GSC | HC-CLEANER REJECT EXHAUSTING ON/OFF VALVE OPENED CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD203 |  | TM140317HS031E | TM140317SV031E.ZSO | TM140317SV031E.GSO | HC-CLEANER REJECT EXHAUSTING ON/OFF VALVE OPENED OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD203 | TM1403ASD202 | TM140317HS031E | TM140317EV031E | TM140317EV031E | HC-CLEANER REJECT EXHAUSTING ON/OFF VALVE OPENED SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA101 |  | TM140317LC032 | TM140317LT032 | TM140317LT032.MV | THICKENER BROKE TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS034 | TM140317SV034 | TM140317SV034 | BROKE DEFLAKER FLUSHING ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS203 |  | TM140317HS034 | TM140317SV034.ZSC | TM140317SV034.GSC | BROKE DEFLAKER FLUSHING ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS203 |  | TM140317HS034 | TM140317SV034.ZSO | TM140317SV034.GSO | BROKE DEFLAKER FLUSHING ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS203 |  | TM140317HS034 | TM140317EV034 | TM140317EV034 | BROKE DEFLAKER FLUSHING ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS035 | TM140317SV035 | TM140317SV035 | BROKE DEFLAKER FEED ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS203 |  | TM140317HS035 | TM140317SV035.ZSC | TM140317SV035.GSC | BROKE DEFLAKER FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS203 |  | TM140317HS035 | TM140317SV035.ZSO | TM140317SV035.GSO | BROKE DEFLAKER FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS203 |  | TM140317HS035 | TM140317EV035 | TM140317EV035 | BROKE DEFLAKER FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS036 | TM140317SV036 | TM140317SV036 | BROKE DEFLAKER ACCEPT ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS203 |  | TM140317HS036 | TM140317SV036.ZSC | TM140317SV036.GSC | BROKE DEFLAKER ACCEPT ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS203 |  | TM140317HS036 | TM140317SV036.ZSO | TM140317SV036.GSO | BROKE DEFLAKER ACCEPT ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS203 |  | TM140317HS036 | TM140317EV036 | TM140317EV036 | BROKE DEFLAKER ACCEPT ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS037 | TM140317SV037 | TM140317SV037 | BROKE DEFLAKER BYPASS ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS203 |  | TM140317HS037 | TM140317SV037.ZSC | TM140317SV037.GSC | BROKE DEFLAKER BYPASS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS203 |  | TM140317HS037 | TM140317SV037.ZSO | TM140317SV037.GSO | BROKE DEFLAKER BYPASS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS203 |  | TM140317HS037 | TM140317EV037 | TM140317EV037 | BROKE DEFLAKER BYPASS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA201 |  | TM140317PI038 | TM140317PT038 | TM140317PT038.MV | BROKE DEFLAKER FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317FC039 | TM140317FE039 |  | STOCK TO BROKE DEFLAKED CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA101 |  | TM140317FC039 | TM140317FT039 | TM140317FT039.MV | STOCK TO BROKE DEFLAKED CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 720 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA101 | TM1403ASD101 | TM140317FC039 | TM140317FV039 | TM140317FV039.OUT | STOCK TO BROKE DEFLAKED CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317WC040 | TM140317WX040 | TM140317WX040.SOF | BROKE DEFLAKER SEC SETPOINT | WX | DCS software function | DCS | DCS |  | Software function
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD201 |  | TM140317FS041 | TM140317FS041 | TM140317FS041.L | SEALING WATER TO BROKE DEFLAKER FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA112 |  | TM140317LC042 | TM140317LT042 | TM140317LT042.MV | BROKE DEFLAKED CHEST LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA112 | TM1403ASD112 | TM140317LC042 | TM140317LV042 | TM140317LV042.OUT | BROKE DEFLAKED CHEST LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317NC044 | TM140317NE044 |  | DEFLAKED BROKE TO MIXING CHEST CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230 VAC | [24 empty] | B
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA112 |  | TM140317NC044 | TM140317NT044 | TM140317NT044.MV | DEFLAKED BROKE TO MIXING CHEST CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 6 | %Cs | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD111 |  | TM140317NC044 | TM140317NS044 | TM140317NS044.MV | DEFLAKED BROKE TO MIXING CHEST CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA112 | TM1403ASD112 | TM140317NC044 | TM140317NV044 | TM140317NV044.OUT | DEFLAKED BROKE TO MIXING CHEST CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS046 | TM140317SV046 | TM140317SV046 | BROKE DEFLAKED CHEST OUTLET ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS112 |  | TM140317HS046 | TM140317SV046.ZSC | TM140317SV046.GSC | BROKE DEFLAKED CHEST OUTLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS112 |  | TM140317HS046 | TM140317SV046.ZSO | TM140317SV046.GSO | BROKE DEFLAKED CHEST OUTLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS112 |  | TM140317HS046 | TM140317EV046 | TM140317EV046 | BROKE DEFLAKED CHEST OUTLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS048 | TM140317SV048 | TM140317SV048 | SEALING WATER TO YANKEE PULPER AGITATOR ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS103 |  | TM140317HS048 | TM140317SV048.ZSC | TM140317SV048.GSC | SEALING WATER TO YANKEE PULPER AGITATOR ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS103 |  | TM140317HS048 | TM140317SV048.ZSO | TM140317SV048.GSO | SEALING WATER TO YANKEE PULPER AGITATOR ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS103 |  | TM140317HS048 | TM140317EV048 | TM140317EV048 | SEALING WATER TO YANKEE PULPER AGITATOR ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA112 |  | TM140317PC049 | TM140317PT049 | TM140317PT049.MV | BROKE DEFLAKED CHEST PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 4 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS051 | TM140317SV051 | TM140317SV051 | SEALING WATER TO BROKE DEFLAKER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS203 |  | TM140317HS051 | TM140317SV051.ZSC | TM140317SV051.GSC | SEALING WATER TO BROKE DEFLAKER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS203 |  | TM140317HS051 | TM140317SV051.ZSO | TM140317SV051.GSO | SEALING WATER TO BROKE DEFLAKER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS203 |  | TM140317HS051 | TM140317EV051 | TM140317EV051 | SEALING WATER TO BROKE DEFLAKER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA201 |  | TM140317PI052 | TM140317PT052 | TM140317PT052.MV | BROKE DEFLAKER ACCEPT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD201 |  | TM140317TS053 | TM140317TS053 | TM140317TS053.H | BROKE DEFLAKER OUTLET TEMPERATURE HIGH | TS | Temperature switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [7 empty] | Temp. High | Not Temp. High | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS055 | TM140317SV055 | TM140317SV055 | SHOWER WATER TO YANKEE PULPER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS103 |  | TM140317HS055 | TM140317SV055.ZSC | TM140317SV055.GSC | SHOWER WATER TO YANKEE PULPER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS103 |  | TM140317HS055 | TM140317SV055.ZSO | TM140317SV055.GSO | SHOWER WATER TO YANKEE PULPER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS103 |  | TM140317HS055 | TM140317EV055 | TM140317EV055 | SHOWER WATER TO YANKEE PULPER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA112 | TM1404ASD113 | TM140317HC056 | TM140317HV056 | TM140317HV056.OUT | BROKE INTERIM TOWER PUMP OUTLET CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317KS057 | TM140317SV057A | TM140317SV057A | BROKE THICKENER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS201 |  | TM140317KS057 | TM140317SV057A.ZSC | TM140317SV057A.GSC | BROKE THICKENER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS201 |  | TM140317KS057 | TM140317SV057A.ZSO | TM140317SV057A.GSO | BROKE THICKENER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS201 |  | TM140317KS057 | TM140317EV057A | TM140317EV057A | BROKE THICKENER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD201 | TM1403ASD201 | TM140317KS057 | TM140317EV057B | TM140317EV057B | BROKE THICKENER ON/OFF VALVE CLOSED SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD201 | TM1403ASD201 | TM140317KS057 | TM140317EV057C | TM140317EV057C | BROKE THICKENER ON/OFF VALVE OPENED SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS058 | TM140317SV058 | TM140317SV058 | BROKE THICKENER TANK PUMP INLET ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS101 |  | TM140317HS058 | TM140317SV058.ZSC | TM140317SV058.GSC | BROKE THICKENER TANK PUMP INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS101 |  | TM140317HS058 | TM140317SV058.ZSO | TM140317SV058.GSO | BROKE THICKENER TANK PUMP INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS101 |  | TM140317HS058 | TM140317EV058 | TM140317EV058 | BROKE THICKENER TANK PUMP INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS061 | TM140317SV061 | TM140317SV061 | BROKE DEFLAKED CHEST PUMP OUTLET TO MIXING CHEST ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS112 |  | TM140317HS061 | TM140317SV061.ZSC | TM140317SV061.GSC | BROKE DEFLAKED CHEST PUMP OUTLET TO MIXING CHEST ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS112 |  | TM140317HS061 | TM140317SV061.ZSO | TM140317SV061.GSO | BROKE DEFLAKED CHEST PUMP OUTLET TO MIXING CHEST ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS112 |  | TM140317HS061 | TM140317EV061 | TM140317EV061 | BROKE DEFLAKED CHEST PUMP OUTLET TO MIXING CHEST ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317HS062 | TM140317SV062 | TM140317SV062 | BROKE DEFLAKED CHEST PUMP OUTLET TO BROKE THICKENER TANK ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS112 |  | TM140317HS062 | TM140317SV062.ZSC | TM140317SV062.GSC | BROKE DEFLAKED CHEST PUMP OUTLET TO BROKE THICKENER TANK ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS112 |  | TM140317HS062 | TM140317SV062.ZSO | TM140317SV062.GSO | BROKE DEFLAKED CHEST PUMP OUTLET TO BROKE THICKENER TANK ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBS112 |  | TM140317HS062 | TM140317EV062 | TM140317EV062 | BROKE DEFLAKED CHEST PUMP OUTLET TO BROKE THICKENER TANK ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 |  |  | TM140317NC091 | TM140317NE091 |  | BROKE THICKENER TANK PUMP OUTLET CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230 VAC | [24 empty] | B
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA101 |  | TM140317NC091 | TM140317NT091 | TM140317NT091.MV | BROKE THICKENER TANK PUMP OUTLET CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 6 | %Cs | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD101 |  | TM140317NC091 | TM140317NS091 | TM140317NS091.MV | BROKE THICKENER TANK PUMP OUTLET CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBA101 | TM1403ASD101 | TM140317NC091 | TM140317NV091 | TM140317NV091.OUT | BROKE THICKENER TANK PUMP OUTLET CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD102 |  | TM140317XS093 | TM140317XS093A | TM140317EX008A | SHEET BREAK | XS | Web break signals | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Web break | Not Web break | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD102 |  | TM140317XS093 | TM140317XS093B | TM140317EX008B | SHEET BREAK | XS | Web break signals | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Web break | Not Web break | [10 empty] | 1
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM1403JBD101 |  | TM140317FS095 | TM140317FS095 | TM140317FS095.L | SEALING WATER TO BROKE BROKE THICKENER TANK PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
STOCK APPROACH
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320FC001 | TM140320FE001 |  | NBKP#3 REFINED TOWER #1 PUMP TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS | [27 empty] | B
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 |  | TM140320FC001 | TM140320FT001 | TM140320FT001.MV | NBKP#3 REFINED TOWER #1 PUMP TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1000 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 | TM1403ASD111 | TM140320FC001 | TM140320FV001 | TM140320FV001.OUT | NBKP#3 REFINED TOWER #1 PUMP TO MIXING CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320FC002 | TM140320FE002 |  | LBKP 2 INTERMEDIATE TOWER PUMP TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 |  | TM140320FC002 | TM140320FT002 | TM140320FT002.MV | LBKP 2 INTERMEDIATE TOWER PUMP TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 2700 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 | TM1403ASD111 | TM140320FC002 | TM140320FV002 | TM140320FV002.OUT | LBKP 2 INTERMEDIATE TOWER PUMP TO MIXING CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320FC003 | TM140320FE003 |  | BROKE DEFLAKED CHEST PUMP TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 |  | TM140320FC003 | TM140320FT003 | TM140320FT003.MV | BROKE DEFLAKED CHEST PUMP TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 720 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 | TM1403ASD111 | TM140320FC003 | TM140320FV003 | TM140320FV003.OUT | BROKE DEFLAKED CHEST PUMP TO MIXING CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320FC004 | TM140320FE004 |  | SP2 BROKE TOWER PUMP TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 |  | TM140320FC004 | TM140320FT004 | TM140320FT004.MV | SP2 BROKE TOWER PUMP TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1100 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 | TM1403ASD111 | TM140320FC004 | TM140320FV004 | TM140320FV004.OUT | SP2 BROKE TOWER PUMP TO MIXING CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320FC005 | TM140320FE005 |  | RECOVERED STOCK PUMP TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 |  | TM140320FC005 | TM140320FT005 | TM140320FT005.MV | RECOVERED STOCK PUMP TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1800 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320HS006 | TM140320SV006 | TM140320SV006 | SWEETENER PUMP INLET ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS111 |  | TM140320HS006 | TM140320SV006.ZSC | TM140320SV006.GSC | SWEETENER PUMP INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS111 |  | TM140320HS006 | TM140320SV006.ZSO | TM140320SV006.GSO | SWEETENER PUMP INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS111 |  | TM140320HS006 | TM140320EV006 | TM140320EV006 | SWEETENER PUMP INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 |  | TM140320LC008 | TM140320LT008 | TM140320LT008.MV | MIXING CHEST LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 5000 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320HS009 | TM140320SV009 | TM140320SV009 | DILUTION WATER TO SWEETENER PUMP INLET ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS111 |  | TM140320HS009 | TM140320SV009.ZSC | TM140320SV009.GSC | DILUTION WATER TO SWEETENER PUMP INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS111 |  | TM140320HS009 | TM140320SV009.ZSO | TM140320SV009.GSO | DILUTION WATER TO SWEETENER PUMP INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS111 |  | TM140320HS009 | TM140320EV009 | TM140320EV009 | DILUTION WATER TO SWEETENER PUMP INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD111 |  | TM140320FS010 | TM140320FS010 | TM140320FS010.L | SEALING WATER TO SWEETENER PUMP FLOW | FS | Flow Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320HS011 | TM140320SV011 | TM140320SV011 | MIXING CHEST DISCHAGE ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS111 |  | TM140320HS011 | TM140320SV011.ZSC | TM140320SV011.GSC | MIXING CHEST DISCHAGE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS111 |  | TM140320HS011 | TM140320SV011.ZSO | TM140320SV011.GSO | MIXING CHEST DISCHAGE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS111 |  | TM140320HS011 | TM140320EV011 | TM140320EV011 | MIXING CHEST DISCHAGE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320NC012 | TM140320NE012 |  | MIXING CHEST PUMP OUTLET CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230 VAC | [24 empty] | B
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 |  | TM140320NC012 | TM140320NT012 | TM140320NT012.MV | MIXING CHEST PUMP OUTLET CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 6 | %C | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD111 |  | TM140320NC012 | TM140320NS012 | TM140320NS012.MV | MIXING CHEST PUMP OUTLET CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 | TM1403ASD111 | TM140320NC012 | TM140320NV012 | TM140320NV012.OUT | MIXING CHEST PUMP OUTLET CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD111 |  | TM140320FS014 | TM140320FS014 | TM140320FS014.L | SEALING WATER TO MIXING CHEST PUMP 1 FLOW | FS | Flow Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320FC015 | TM140320FE015 |  | NBKP#3 REFINED TOWER #2 PUMP1 TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS | [27 empty] | B
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 |  | TM140320FC015 | TM140320FT015 | TM140320FT015.MV | NBKP#3 REFINED TOWER #2 PUMP1 TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1000 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 | TM1403ASD111 | TM140320FC015 | TM140320FV015 | TM140320FV015.OUT | NBKP#3 REFINED TOWER #2 PUMP1 TO MIXING CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA201 |  | TM140320PI021 | TM140320PT021 | TM140320PT021.MV | TICKLER REFINER FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320CB01 |  | TM140320PI021 | TM140320PI021 | TM140320PI021.IND | TICKLER REFINER FEED PRESSURE | PI | Local digital indicator | Field | DCS | AO | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA201 |  | TM140320PI022 | TM140320PT022 | TM140320PT022.MV | TICKLER REFINER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320CB01 |  | TM140320PI022 | TM140320PI022 | TM140320PI022.IND | TICKLER REFINER OUTLET PRESSURE | PI | Local digital indicator | Field | DCS | AO | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320HS024 | TM140320SV024 | TM140320SV024 | TICKLER REFINER FEED ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS204 |  | TM140320HS024 | TM140320SV024.ZSC | TM140320SV024.GSC | TICKLER REFINER FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS204 |  | TM140320HS024 | TM140320SV024.ZSO | TM140320SV024.GSO | TICKLER REFINER FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS204 |  | TM140320HS024 | TM140320EV024 | TM140320EV024 | TICKLER REFINER FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320HS025 | TM140320SV025 | TM140320SV025 | TICKLER REFINER ACCEPT ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS204 |  | TM140320HS025 | TM140320SV025.ZSC | TM140320SV025.GSC | TICKLER REFINER ACCEPT ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS204 |  | TM140320HS025 | TM140320SV025.ZSO | TM140320SV025.GSO | TICKLER REFINER ACCEPT ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS204 |  | TM140320HS025 | TM140320EV025 | TM140320EV025 | TICKLER REFINER ACCEPT ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320HS026 | TM140320SV026 | TM140320SV026 | TICKLER REFINER BYPASS ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS204 |  | TM140320HS026 | TM140320SV026.ZSC | TM140320SV026.GSC | TICKLER REFINER BYPASS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS204 |  | TM140320HS026 | TM140320SV026.ZSO | TM140320SV026.GSO | TICKLER REFINER BYPASS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS204 |  | TM140320HS026 | TM140320EV026 | TM140320EV026 | TICKLER REFINER BYPASS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320HS027 | TM140320SV027 | TM140320SV027 | DILUTION WATER TO TICKLER REFINER FEED ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS204 |  | TM140320HS027 | TM140320SV027.ZSC | TM140320SV027.GSC | DILUTION WATER TO TICKLER REFINER FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS204 |  | TM140320HS027 | TM140320SV027.ZSO | TM140320SV027.GSO | DILUTION WATER TO TICKLER REFINER FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS204 |  | TM140320HS027 | TM140320EV027 | TM140320EV027 | DILUTION WATER TO TICKLER REFINER FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320HS028 | TM140320SV028 | TM140320SV028 | SEALING WATER TO TICKLER REFINER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS204 |  | TM140320HS028 | TM140320SV028.ZSC | TM140320SV028.GSC | SEALING WATER TO TICKLER REFINER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS204 |  | TM140320HS028 | TM140320SV028.ZSO | TM140320SV028.GSO | SEALING WATER TO TICKLER REFINER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS204 |  | TM140320HS028 | TM140320EV028 | TM140320EV028 | SEALING WATER TO TICKLER REFINER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD202 |  | TM140320FS029 | TM140320FS029 | TM140320FS029.L | SEALING WATER TO TICKLER REFINER FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320TIZ030 | TM140320TE030 |  | TICKLER REFINER OUTLET TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | B | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA201 |  | TM140320TIZ030 | TM140320TT030 | TM140320TT030.MV | TICKLER REFINER OUTLET TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD202 |  | TM140320TIZ030 | TM140320TS030 | TM140320TS030.H | TICKLER REFINER OUTLET TEMPERATURE HIGH | TS | Temperature switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 150 | ˚C | [7 empty] | Temp. High | Not Temp. High | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD202 |  | TM140320GS031 | TM140320GS031.A | TM140320GS031.A.START | TICKLER REFINER FILLINGS POSITION START | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Start | Start | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD202 |  | TM140320GS031 | TM140320GS031.B | TM140320GS031.B.OPEN | TICKLER REFINER FILLINGS POSITION OPEN | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD202 |  | TM140320GS031 | TM140320GS031.C | TM140320GS031.C.SAF | TICKLER REFINER FILLINGS POSITION SAFETY | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Safety | Safety | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320EC033 | TM140320ET033 | TM140320ET033.MV | TICKLER REFINER POWER | ET | Power transmitter | MCC | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | MCC | 0 | 355 | kW
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320CB01 |  | TM140320EC033 | TM140320EI033 | TM140320EI033.IND | TICKLER REFINER POWER | EI | Local digital indicator | Field | DCS | AO | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 100 | % | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320FC034 | TM140320FE034 |  | TICKLER REFINER TO MACHINE CHEST FLOW | FE | Magnetic flow Sensor | Field
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 |  | TM140320FC034 | TM140320FT034 | TM140320FT034.MV | TICKLER REFINER TO MACHINE CHEST FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 3600 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 | TM1403ASD111 | TM140320FC034 | TM140320FV034 | TM140320FV034.OUT | TICKLER REFINER TO MACHINE CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320FC035 | TM140320FE035 |  | TICKLER REFINER RECIRCULATION FLOW | FE | Magnetic flow Sensor | Field
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 |  | TM140320FC035 | TM140320FT035 | TM140320FT035.MV | TICKLER REFINER RECIRCULATION FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1800 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 | TM1403ASD111 | TM140320FC035 | TM140320FV035 | TM140320FV035.OUT | TICKLER REFINER RECIRCULATION FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320WC036 | TM140320WX036 | TM140320WX036.SOF | TICKLER REFINER PRODUCTION | WX | DCS software function | DCS | DCS |  | Software function
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320AI037 | TM140320AE037 |  | TICKLER REFINER FREENESS | AE | Freeness sensor | Field
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 |  | TM140320AI037 | TM140320AT037 | TM140320AT037.MV | TICKLER REFINER FREENESS | AT | Freeness transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 15 | 750 | ml CSF | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD111 |  | TM140320AI037 | TM140320AS037 | TM140320AS037.MV | TICKLER REFINER FREENESS | AS | Freeness transmitter Stop Sampling | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320XS038 | TM140320CB01 | TM110011CB01 | TICKLER REFINER CONTROL | CB | Local Control Box | Field | [28 empty] | 4
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320CB01 |  | TM140320XS038 | TM140320H11 038 | TM140320H11 038.RUN/F | TICKLER REFINER MOTOR RUN / FAULT | H1 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Run | Run | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320CB01 |  | TM140320XS038 | TM140320H21 038 | TM140320H21 038.L/F | TICKLER REFINER LOAD / FAULT | H2 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Load | Load | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320CB01 |  | TM140320XS038 | TM140320H22 038 | TM140320H22 038.REL/F | TICKLER REFINER RELEASE / FAULT | H2 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Release | Release | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320CB01 |  | TM140320XS038 | TM140320H23 038 | TM140320H23 038.FAULT | TICKLER REFINER FAULT | H2 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Fault | Fault | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320CB01 |  | TM140320XS038 | TM140320S10 038 | TM140320S10 038.ESTOP | TICKLER REFINER PANEL E - STOP | S1 | E - Stop Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | E - Stop | Not E - Stop | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320CB01 |  | TM140320XS038 | TM140320S11 038 | TM140320S11 038.START | TICKLER REFINER START | S1 | Illuminated Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Start | Start | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320CB01 |  | TM140320XS038 | TM140320S12 038 | TM140320S12 038.STOP | TICKLER REFINER STOP | S1 | Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Stop | Not Stop | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320CB01 |  | TM140320XS038 | TM140320S20 038 | TM140320S20 038.L/D | OPERATING MODE SELECT SWITCH - LOCAL/DCS | S2 | Select Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | DCS | Local | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320CB01 |  | TM140320XS038 | TM140320S21 038 | TM140320S21 038.LOAD | TICKLER REFINER LOAD | S2 | Illuminated Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Load | Load | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320CB01 |  | TM140320XS038 | TM140320S22 038 | TM140320S22 038.RELEASE | TICKLER REFINER RELEASE | S2 | Illuminated Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Release | Release | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320CB01 |  | TM140320XS038 | TM140320S23 038 | TM140320S23 038.FAST | TICKLER REFINER FAST | S2 | Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Fast | Fast | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320CB01 |  | TM140320XS038 | TM140320S24 038 | TM140320S24 038.TEST | TICKLER REFINER CB LAMP TEST | S2 | Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Lamp Test | Lamp Test | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320EC039 | TM140320EX039 | TM140320EX039.SOF | TICKLER REFINER POWER | EX | DCS software function | DCS | DCS |  | Software function | [25 empty] | B
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 |  | TM140320PC045 | TM140320PT045 | TM140320PT045.MV | SWEETENER PUMP OUTLET OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 |  | TM140320LC051 | TM140320LT051 | TM140320LT051.MV | MACHINE CHEST LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 5000 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320HS052 | TM140320SV052 | TM140320SV052 | MACHINE CHEST DISCHAGE ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS112 |  | TM140320HS052 | TM140320SV052.ZSC | TM140320SV052.GSC | MACHINE CHEST DISCHAGE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS112 |  | TM140320HS052 | TM140320SV052.ZSO | TM140320SV052.GSO | MACHINE CHEST DISCHAGE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS112 |  | TM140320HS052 | TM140320EV052 | TM140320EV052 | MACHINE CHEST DISCHAGE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320NC053 | TM140320NE053 |  | MACHINE CHEST PUMP OUTLET CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230 VAC
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 |  | TM140320NC053 | TM140320NT053 | TM140320NT053.MV | MACHINE CHEST PUMP OUTLET CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 6 | %C | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD111 |  | TM140320NC053 | TM140320NS053 | TM140320NS053.MV | MACHINE CHEST PUMP OUTLET CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 | TM1403ASD111 | TM140320NC053 | TM140320NV053 | TM140320NV053.OUT | MACHINE CHEST PUMP OUTLET CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA111 |  | TM140320PC054 | TM140320PT054 | TM140320PT054.MV | MACHINE CHEST PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320FC055 | TM140320FE055 |  | MACHINE CHEST PUMP OUTLET FLOW | FE | Magnetic flow Sensor | Field
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA102 |  | TM140320FC055 | TM140320FT055 | TM140320FT055.MV | MACHINE CHEST PUMP OUTLET FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 3600 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320FC055 | TM140320FV055 | TM140320FV055.OUT | MACHINE CHEST PUMP OUTLET FLOW CV SETPOINT | FV | Basic Weight Valve | [29 empty] | C
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA102 |  | TM140320FC055 | TM140320FY055 | TM140320FY055.MV | MACHINE CHEST PUMP OUTLET FLOW CV POSITION FEEDBACK | FY | Valve Position Feedback | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD101 |  | TM140320FC055 | TM140320FV055.ZSC | TM140320FV055.GSC | MACHINE CHEST PUMP OUTLET FLOW CV CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD101 |  | TM140320FC055 | TM140320FV055.ZSO | TM140320FV055.GSO | MACHINE CHEST PUMP OUTLET FLOW CV OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD101 |  | TM140320FC055 | TM140320FV055.STP | TM140320FV055.STP | MACHINE CHEST PUMP OUTLET FLOW CV CLOSE COMMAND | STP | Close Command | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [11 empty] | Close | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD101 |  | TM140320FC055 | TM140320FV055.STO | TM140320FV055.STO | MACHINE CHEST PUMP OUTLET FLOW CV OPEN COMMAND | STO | Open Command | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [11 empty] | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD111 |  | TM140320FS057 | TM140320FS057 | TM140320FS057.L | SEALING WATER TO MACHINE CHEST PUMP 1 FLOW | FS | Flow Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA202 |  | TM140320LI061 | TM140320LT061 | TM140320LT061.MV | SILO LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3000 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320HS062 | TM140320SV062 | TM140320SV062 | WHITE WATER TO SILO ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS205 |  | TM140320HS062 | TM140320SV062.ZSC | TM140320SV062.GSC | WHITE WATER TO SILO ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS205 |  | TM140320HS062 | TM140320SV062.ZSO | TM140320SV062.GSO | WHITE WATER TO SILO ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS205 |  | TM140320HS062 | TM140320EV062 | TM140320EV062 | WHITE WATER TO SILO ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140335TC020 | TM140335TE020 |  | SILO TEMPERATURE | TE | Temperature Sensor | Field
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA202 |  | TM140335TC020 | TM140335TT020 | TM140335TT020.MV | SILO TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA202 | TM1403ASD201 | TM140335TC020 | TM140335TV020 | TM140335TV020.OUT | SILO TEMPERATURE CV SETPOINT | TV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320AI064 | TM140320AE064 |  | SILO CHANNEL OVERFLOW PARTICLE CHARGE DETECT | AE | PCD sensor | Field | DCS
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA202 |  | TM140320AI064 | TM140320AT064 | TM140320AT064.MV | SILO CHANNEL OVERFLOW PARTICLE CHARGE DETECT | AT | PCD transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | -150 | -30 | µEQ/l | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD202 |  | TM140320AI064 | TM140320AS064 | TM140320AS064.INT | SILO CHANNEL OVERFLOW PARTICLE CHARGE INTERLOCK | AS | PCD transmitter Stop Sampling | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320AC065 | TM140320AE065 |  | SILO PH | AE | pH Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA202 |  | TM140320AC065 | TM140320AT065 | TM140320AT065.MV | SILO PH | AT | pH Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 14 | Ph | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320HS066 | TM140320SV066 | TM140320SV066 | MACHINE CHEST PUMP OUTLET TO SILO ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 0
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS102 |  | TM140320HS066 | TM140320SV066.ZSC | TM140320SV066.GSC | MACHINE CHEST PUMP OUTLET TO SILO ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS102 |  | TM140320HS066 | TM140320SV066.ZSO | TM140320SV066.GSO | MACHINE CHEST PUMP OUTLET TO SILO ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS102 |  | TM140320HS066 | TM140320EV066 | TM140320EV066 | MACHINE CHEST PUMP OUTLET TO SILO ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320HS067 | TM140320SV067 | TM140320SV067 | MACHINE CHEST PUMP OUTLET TO RECOVERED STOCK CHEST ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 0
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS102 |  | TM140320HS067 | TM140320SV067.ZSC | TM140320SV067.GSC | MACHINE CHEST PUMP OUTLET TO RECOVERED STOCK CHEST ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS102 |  | TM140320HS067 | TM140320SV067.ZSO | TM140320SV067.GSO | MACHINE CHEST PUMP OUTLET TO RECOVERED STOCK CHEST ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS102 |  | TM140320HS067 | TM140320EV067 | TM140320EV067 | MACHINE CHEST PUMP OUTLET TO RECOVERED STOCK CHEST ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320HS072 | TM140320SV072 | TM140320SV072 | SEALING WATER TO FAN PUMP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS101 |  | TM140320HS072 | TM140320SV072.ZSC | TM140320SV072.GSC | SEALING WATER TO FAN PUMP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS101 |  | TM140320HS072 | TM140320SV072.ZSO | TM140320SV072.GSO | SEALING WATER TO FAN PUMP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS101 |  | TM140320HS072 | TM140320EV072 | TM140320EV072 | SEALING WATER TO FAN PUMP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD101 |  | TM140320FS073 | TM140320FS073 | TM140320FS073.L | SEALING WATER TO FAN PUMP FLOW L A | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320HS075 | TM140320SV075 | TM140320SV075 | FAN PUMP OUTLET ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS101 |  | TM140320HS075 | TM140320SV075.ZSC | TM140320SV075.GSC | FAN PUMP OUTLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS101 |  | TM140320HS075 | TM140320SV075.ZSO | TM140320SV075.GSO | FAN PUMP OUTLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS101 |  | TM140320HS075 | TM140320EV075 | TM140320EV075 | FAN PUMP OUTLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA102 | TM1403ASD102 | TM140320HC078 | TM140320HV078 | TM140320HV078.OUT | 1ST STAGE APPROACH SCREEN REJECT CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320XI079 | TM140320XE079 |  | 1ST STAGE APPROACH SCREEN MOTOR VIBRATION 1 | XE | Vibration sensor | Field | [28 empty] | C | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA102 |  | TM140320XI079 | TM140320XT079 | TM140320XT079.MV | 1ST STAGE APPROACH SCREEN MOTOR VIBRATION 1 | XT | Vibration transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | [22 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA102 |  | TM140320PI081 | TM140320PT081 | TM140320PT081.MV | 1ST STAGE APPROACH SCREEN FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA102 |  | TM140320PI082 | TM140320PT082 | TM140320PT082.MV | 1ST STAGE APPROACH SCREEN ACCEPT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320PDI083 | TM140320PDX083 | TM140320PDX083.SOF | 1ST STAGE APPROACH SCREEN DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320FI084 | TM140320FE084 |  | 1ST STAGE APPROACH SCREEN REJECT FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | B
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA102 |  | TM140320FI084 | TM140320FT084 | TM140320FT084.MV | 1ST STAGE APPROACH SCREEN REJECT FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 2000 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320HS085 | TM140320SV085 | TM140320SV085 | FROM 1ST STAGE APPROACH SCREENTO SILO CHANNEL ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS101 |  | TM140320HS085 | TM140320SV085.ZSC | TM140320SV085.GSC | FROM 1ST STAGE APPROACH SCREENTO SILO CHANNEL ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS101 |  | TM140320HS085 | TM140320SV085.ZSO | TM140320SV085.GSO | FROM 1ST STAGE APPROACH SCREENTO SILO CHANNEL ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS101 |  | TM140320HS085 | TM140320EV085 | TM140320EV085 | FROM 1ST STAGE APPROACH SCREENTO SILO CHANNEL ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320HS086 | TM140320SV086 | TM140320SV086 | SEALING WATER TO 1ST STAGE APPROACH SCREEN ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS101 |  | TM140320HS086 | TM140320SV086.ZSC | TM140320SV086.GSC | SEALING WATER TO 1ST STAGE APPROACH SCREEN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS101 |  | TM140320HS086 | TM140320SV086.ZSO | TM140320SV086.GSO | SEALING WATER TO 1ST STAGE APPROACH SCREEN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS101 |  | TM140320HS086 | TM140320EV086 | TM140320EV086 | SEALING WATER TO 1ST STAGE APPROACH SCREEN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD101 |  | TM140320FS087 | TM140320FS087 | TM140320FS087.L | SEALING WATER TO 1ST STAGE APPROACH SCREEN FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA201 |  | TM140320PI091 | TM140320PT091 | TM140320PT091.MV | 2ND STAGE APPROACH SCREEN FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA201 |  | TM140320PI092 | TM140320PT092 | TM140320PT092.MV | 2ND STAGE APPROACH SCREEN ACCEPT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320PDI093 | TM140320PDX093 | TM140320PDX093.SOF | 2ND STAGE APPROACH SCREEN DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320KC094 | TM140320SV094 | TM140320SV094 | 2ND STAGE APPROACH SCREEN REJECT ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD202 |  | TM140320KC094 | TM140320SV094.ZSC | TM140320SV094.GSC | 2ND STAGE APPROACH SCREEN REJECT ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD202 |  | TM140320KC094 | TM140320SV094.ZSO | TM140320SV094.GSO | 2ND STAGE APPROACH SCREEN REJECT ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD202 | TM1403ASD201 | TM140320KC094 | TM140320EV094 | TM140320EV094 | 2ND STAGE APPROACH SCREEN REJECT ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA201 | TM1403ASD201 | TM140320HC095 | TM140320HV095 | TM140320HV095.OUT | FROM 2ND STAGE APPROACH SCREEN TO SILO CHANNEL CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320HS096 | TM140320SV096 | TM140320SV096 | SEALING WATER TO 2ND STAGE APPROACH SCREEN ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS203 |  | TM140320HS096 | TM140320SV096.ZSC | TM140320SV096.GSC | SEALING WATER TO 2ND STAGE APPROACH SCREEN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS203 |  | TM140320HS096 | TM140320SV096.ZSO | TM140320SV096.GSO | SEALING WATER TO 2ND STAGE APPROACH SCREEN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBS203 |  | TM140320HS096 | TM140320EV096 | TM140320EV096 | SEALING WATER TO 2ND STAGE APPROACH SCREEN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBD202 |  | TM140320FS097 | TM140320FS097 | TM140320FS097.L | SEALING WATER TO 2ND STAGE APPROACH SCREEN FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA102 |  | TM140320LC101 | TM140320LT101 | TM140320LT101.MV | WIRE WHITE WATER TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3300 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA102 | TM1403ASD102 | TM140320HC103 | TM140320HV103 | TM140320HV103.OUT | W.W OVERFLOW CHEST PUMP TO SILO CHANNEL CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA102 | TM1403ASD102 | TM140320HC104 | TM140320HV104 | TM140320HV104.OUT | W.W OVERFLOW CHEST PUMP TO W.W COLLECTION TANK CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320XI106 | TM140320XE106 |  | 1ST STAGE APPROACH SCREEN MOTOR VIBRATION 2 | XE | Vibration sensor | Field | [28 empty] | C | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA102 |  | TM140320XI106 | TM140320XT106 | TM140320XT106.MV | 1ST STAGE APPROACH SCREEN MOTOR VIBRATION 2 | XT | Vibration transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | [22 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA202 |  | TM140320PC111 | TM140320PT111 | TM140320PT111.MV | HEADBOX PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA102 | TM1403ASD102 | TM140320HC112 | TM140320HV112 | TM140320HV112.OUT | HEADBOX RECIRCULATION CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140320 |  |  | TM140320FI114 | TM140320FE114 |  | HEADBOX RECIRCULATION FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | B
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM1403JBA102 |  | TM140320FI114 | TM140320FT114 | TM140320FT114.MV | HEADBOX RECIRCULATION FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 5000 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140315 |  |  | TM140315FC005 | TM140315FE005 |  | WET STRENGHT AGENT TO MIXING CHEST PUMP FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3701 | TM140315 | TM1403JBA111 |  | TM140315FC005 | TM140315FT005 | TM140315FT005.MV | WET STRENGHT AGENT TO MIXING CHEST PUMP FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | hold | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140315 |  |  | TM140315FC006 | TM140315FE006 |  | DRY STRENGHT AGENT TO MACHINE CHEST PUMP FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3701 | TM140315 | TM1403JBA111 |  | TM140315FC006 | TM140315FT006 | TM140315FT006.MV | DRY STRENGHT AGENT TO MACHINE CHEST PUMP FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | hold | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140315 |  |  | TM140315FC007 | TM140315FE007 |  | SOFT AGENT TO MIXING CHEST PUMP FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3701 | TM140315 | TM1403JBA111 |  | TM140315FC007 | TM140315FT007 | TM140315FT007.MV | SOFT AGENT TO MIXING CHEST PUMP FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | hold | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140315 |  |  | TM140315FC008 | TM140315FE008 |  | CMC TO FAN PUMP FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3701 | TM140315 | TM1403JBA102 |  | TM140315FC008 | TM140315FT008 | TM140315FT008.MV | CMC TO FAN PUMP FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | hold | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140315 |  |  | TM140315HS069 | TM140315SV069 | TM140315SV069 | WET STRENGHT AGENT TO MIXING CHEST PUMP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3701 | TM140315 | TM1403JBS111 |  | TM140315HS069 | TM140315SV069.ZSC | TM140315SV069.GSC | WET STRENGHT AGENT TO MIXING CHEST PUMP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140315 | TM1403JBS111 |  | TM140315HS069 | TM140315SV069.ZSO | TM140315SV069.GSO | WET STRENGHT AGENT TO MIXING CHEST PUMP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140315 | TM1403JBS111 |  | TM140315HS069 | TM140315EV069 | TM140315EV069 | WET STRENGHT AGENT TO MIXING CHEST PUMP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140315 |  |  | TM140315HS070 | TM140315SV070 | TM140315SV070 | DRY STRENGHT AGENT TO MACHINE CHEST PUMP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3701 | TM140315 | TM1403JBS112 |  | TM140315HS070 | TM140315SV070.ZSC | TM140315SV070.GSC | DRY STRENGHT AGENT TO MACHINE CHEST PUMP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140315 | TM1403JBS112 |  | TM140315HS070 | TM140315SV070.ZSO | TM140315SV070.GSO | DRY STRENGHT AGENT TO MACHINE CHEST PUMP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140315 | TM1403JBS112 |  | TM140315HS070 | TM140315EV070 | TM140315EV070 | DRY STRENGHT AGENT TO MACHINE CHEST PUMP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140315 |  |  | TM140315HS071 | TM140315SV071 | TM140315SV071 | SOFT AGENT TO MIXING CHEST PUMP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3701 | TM140315 | TM1403JBS111 |  | TM140315HS071 | TM140315SV071.ZSC | TM140315SV071.GSC | SOFT AGENT TO MIXING CHEST PUMP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140315 | TM1403JBS111 |  | TM140315HS071 | TM140315SV071.ZSO | TM140315SV071.GSO | SOFT AGENT TO MIXING CHEST PUMP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140315 | TM1403JBS111 |  | TM140315HS071 | TM140315EV071 | TM140315EV071 | SOFT AGENT TO MIXING CHEST PUMP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140315 |  |  | TM140315HS072 | TM140315SV072 | TM140315SV072 | CMC TO FAN PUMP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3701 | TM140315 | TM1403JBS101 |  | TM140315HS072 | TM140315SV072.ZSC | TM140315SV072.GSC | CMC TO FAN PUMP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140315 | TM1403JBS101 |  | TM140315HS072 | TM140315SV072.ZSO | TM140315SV072.GSO | CMC TO FAN PUMP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3701 | TM140315 | TM1403JBS101 |  | TM140315HS072 | TM140315EV072 | TM140315EV072 | CMC TO FAN PUMP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
WHITE WATER AND FIBRE RECOVERY
P-OKITM07-10-320-07-PID-3705 | TM140321 |  |  | TM140321FC001 | TM140321FE001 |  | W.W TO DISC FILTER FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA111 |  | TM140321FC001 | TM140321FT001 | TM140321FT001.MV | W.W TO DISC FILTER FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 5000 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA111 | TM1403ASD112 | TM140321FC001 | TM140321FV001 | TM140321FV001.OUT | W.W TO DISC FILTER FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA101 |  | TM140321LC002 | TM140321LT002 | TM140321LT002.MV | SUPER CLARIFIED TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA101 | TM1403ASD101 | TM140321LC002 | TM140321LV002 | TM140321LV002.OUT | SUPER CLARIFIED TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 |  |  | TM140321FFC003 | TM140321FE003 |  | SWEETENER STOCK FLOW | FE | Magnetic flow Sensor | Field
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA111 |  | TM140321FFC003 | TM140321FT003 | TM140321FT003.MV | SWEETENER STOCK FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1800 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA111 | TM1403ASD112 | TM140321FFC003 | TM140321FV003 | TM140321FV003.OUT | SWEETENER STOCK FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA101 |  | TM140321LC004 | TM140321LT004 | TM140321LT004.MV | CLARIFIED TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA101 | TM1403ASD101 | TM140321LC004 | TM140321LV004 | TM140321LV004.OUT | CLARIFIED TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA101 |  | TM140321LC005 | TM140321LT005 | TM140321LT005.MV | CLOUDY FILTRATE TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3300 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA101 | TM1403ASD101 | TM140321LC005 | TM140321LV005 | TM140321LV005.OUT | CLOUDY FILTRATE TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA101 |  | TM140321LC006 | TM140321LT006 | TM140321LT006.MV | RECOVERED STOCK CHEST LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA111 |  | TM140321LC007 | TM140321LT007 | TM140321LT007.MV | W.W. COLLECTION TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10000 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA111 | TM1403ASD112 | TM140321LC007 | TM140321LV007A | TM140321LV007A.OUT | W.W. COLLECTION TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA111 | TM1403ASD112 | TM140321LC007 | TM140321LV007B | TM140321LV007B.PRO | W.W. COLLECTION TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA101 |  | TM140321PI008 | TM140321PT008 | TM140321PT008.MV | CWW LP SHOWER FILTER INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 |  |  | TM140321PDI009 | TM140321PDX009 | TM140321PDX009.SOF | CWW LP SHOWER FILTER DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function |  |  |  | 0 | 2 | Bar.g | [19 empty] | B
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA101 |  | TM140321PC010 | TM140321PT010 | TM140321PT010.MV | CWW LP SHOWER FILTER FILTER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 |  |  | TM140321HS011 | TM140321SV011 | TM140321SV011 | W.W TO DISC FILTER SHOWERS ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBS201 |  | TM140321HS011 | TM140321SV011.ZSC | TM140321SV011.GSC | W.W TO DISC FILTER SHOWERS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBS201 |  | TM140321HS011 | TM140321SV011.ZSO | TM140321SV011.GSO | W.W TO DISC FILTER SHOWERS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBS201 |  | TM140321HS011 | TM140321EV011 | TM140321EV011 | W.W TO DISC FILTER SHOWERS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | MCC |  | TM140321EI012 | TM140321ET012 | TM140321ET012.MV | DISC FILTER TORQUE | ET | Power transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA201 |  | TM140321PI013 | TM140321PT013 | TM140321PT013.MV | DISC FILTER VACUUM | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBD201 |  | TM140321SS014 | TM140321GS014A | TM140321GS014A.SEC | DISC FILTER SECTOR COUNTER SECTOR PULSE | GS | Proximity Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Sector Pulse | Sector Pulse | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBD201 |  | TM140321SS014 | TM140321GS014B | TM140321GS014B.ROT | DISC FILTER SECTOR COUNTER ROTATION PULSE | GS | Proximity Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Rotation Pulse | Rotation Pulse | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBD201 |  | TM140321SS015 | TM140321SS015 | TM140321SS015.L | DISC FILTER SPEED REPULPER SPEED LOW | SS | Speed Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Speed Low | Not Speed Low | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBD201 |  | TM140321XS016 | TM140321S9 016 | TM140321S9 016.DCS/LOCAL | DISC FILTER LOCAL OPERATION MAINDRIVE DCS/LOCAL | S9 | Selector Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Jog | Jog | [10 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBD201 |  | TM140321XS016 | TM140321S11 016 | TM140321S11 016.JOG | DISC FILTER LOCAL OPERATION MAINDRIVE JOG FORWARD | S11 | Push button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Local | DCS | [10 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBD201 |  | TM140321XS017 | TM140321S9 017 | TM140321S9 017.JOG | DISC FILTER LOCAL OPERATION SHOWER OSCILLATION DCS/LOCAL | S9 | Selector Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Jog | Jog | [10 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBD201 |  | TM140321XS017 | TM140321S11 017 | TM140321S11 017.DCS/LOCAL | DISC FILTER LOCAL OPERATION SHOWER OSCILLATION LOCAL START | S11 | Push button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Local | DCS | [10 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA101 |  | TM140321PI018 | TM140321PT018 | TM140321PT018.MV | SCWW SHOWER FILTER INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 7 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 |  |  | TM140321PDI019 | TM140321PDX019 | TM140321PDX019.SOF | SCWW SHOWER FILTER DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function |  |  |  | 0 | 2 | Bar.g | [19 empty] | B
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA101 |  | TM140321PC020 | TM140321PT020 | TM140321PT020.MV | SCWW SHOWER FILTER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 7 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA201 |  | TM140321LC021 | TM140321LT021 | TM140321LT021.MV | DISC FILTER LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 2000 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA111 |  | TM140321PC022 | TM140321PT022 | TM140321PT022.MV | TM AREA CRC PUMP OUTLET WHITE WATER PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 7 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA101 |  | TM140321PI024 | TM140321PT024 | TM140321PT024.MV | CWW HP SHOWER FILTER FILTER INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 25 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 |  |  | TM140321PDI025 | TM140321PDX025 | TM140321PDX025.SOF | CWW HP SHOWER FILTER DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function |  |  |  | 0 | 2 | Bar.g | [19 empty] | B
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA101 |  | TM140321PC026 | TM140321PT026 | TM140321PT026.MV | CWW HP SHOWER FILTER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 25 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBD201 |  | TM140321XS028 | TM140321S10 028 | TM140321S10 028.ESTOP | DISC FILTER LOCAL OPERATION MAINDRIVE E-STOP | S10 | E - Stop Push Button | +CP01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | E-Stop | [11 empty] | 4 | Andritz
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321CP01 |  | TM140321XS031 | TM140321S1.031 | TM140321S1.031 | CWW LP SHOWER FILTER LOCAL PANEL | S1 | Differential Pressure High alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321CP01 |  | TM140321XS031 | TM140321S2.031 | TM140321S2.031 | CWW LP SHOWER FILTER LOCAL PANEL | S2 | Flush alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321CP01 |  | TM140321XS031 | TM140321S3.031 | TM140321S3.031 | CWW LP SHOWER FILTER LOCAL PANEL | S3 | Power Failure alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321CP02 |  | TM140321XS032 | TM140321S1.032 | TM140321S1.032 | CWW HP SHOWER FILTER LOCAL PANEL | S1 | Differential Pressure High alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321CP02 |  | TM140321XS032 | TM140321S2.032 | TM140321S2.032 | CWW HP SHOWER FILTER LOCAL PANEL | S2 | Flush alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321CP02 |  | TM140321XS032 | TM140321S3.032 | TM140321S3.032 | CWW HP SHOWER FILTER LOCAL PANEL | S3 | Power Failure alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321CP03 |  | TM140321XS033 | TM140321S1.033 | TM140321S1.033 | SCWW SHOWER FILTER LOCAL PANEL | S1 | Differential Pressure High alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321CP03 |  | TM140321XS033 | TM140321S2.033 | TM140321S2.033 | SCWW SHOWER FILTER LOCAL PANEL | S2 | Flush alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321CP03 |  | TM140321XS033 | TM140321S3.033 | TM140321S3.033 | SCWW SHOWER FILTER LOCAL PANEL | S3 | Power Failure alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-3705 | TM140321 |  |  | TM140321HS036 | TM140321SV036 | TM140321SV036 | W.W TO DISC FILTER SHOWERS ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBS201 |  | TM140321HS036 | TM140321SV036.ZSC | TM140321SV036.GSC | W.W TO DISC FILTER SHOWERS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBS201 |  | TM140321HS036 | TM140321SV036.ZSO | TM140321SV036.GSO | W.W TO DISC FILTER SHOWERS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBS201 |  | TM140321HS036 | TM140321EV036 | TM140321EV036 | W.W TO DISC FILTER SHOWERS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 |  |  | TM140321FC037 | TM140321FE037 |  | W.W TO DISC FILTER REPULPER FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA201 |  | TM140321FC037 | TM140321FT037 | TM140321FT037.MV | W.W TO DISC FILTER REPULPER FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1000 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA201 | TM1403ASD201 | TM140321FC037 | TM140321FV037 | TM140321FV037.OUT | W.W TO DISC FILTER REPULPER FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA201 |  | TM140321PC038 | TM140321PT038 | TM140321PT038.MV | DISC FILTER SHOWERS PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA101 | TM1403ASD101 | TM140321HC039 | TM140321HV039 | TM140321HV039.OUT | FRESH WATER TO CLOUDY FILTRATE TANK CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBD101 |  | TM140321FS040 | TM140321FS040 | TM140321FS040.L | SEALING WATER TO REC PULP CHEST PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA201 |  | TM140321PI041 | TM140321PT041 | TM140321PT041.MV | W.W TO DISC FILTER SHOWERS PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 |  |  | TM140321HS045 | TM140321SV045 | TM140321SV045 | REC PULP CHEST PUMP OUTLET TO BROKE INTERIM TOWER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBS111 |  | TM140321HS045 | TM140321SV045.ZSC | TM140321SV045.GSC | REC PULP CHEST PUMP OUTLET TO BROKE INTERIM TOWER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBS111 |  | TM140321HS045 | TM140321SV045.ZSO | TM140321SV045.GSO | REC PULP CHEST PUMP OUTLET TO BROKE INTERIM TOWER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBS111 |  | TM140321HS045 | TM140321EV045 | TM140321EV045 | REC PULP CHEST PUMP OUTLET TO BROKE INTERIM TOWER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 |  |  | TM140321HS046 | TM140321SV046 | TM140321SV046 | REC PULP CHEST PUMP OUTLET TO TM 14.3 MIXING CHEST ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBS111 |  | TM140321HS046 | TM140321SV046.ZSC | TM140321SV046.GSC | REC PULP CHEST PUMP OUTLET TO TM 14.3 MIXING CHEST ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBS111 |  | TM140321HS046 | TM140321SV046.ZSO | TM140321SV046.GSO | REC PULP CHEST PUMP OUTLET TO TM 14.3 MIXING CHEST ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBS111 |  | TM140321HS046 | TM140321EV046 | TM140321EV046 | REC PULP CHEST PUMP OUTLET TO TM 14.3 MIXING CHEST ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA101 |  | TM140321PC050 | TM140321PT050 | TM140321PT050.MV | CLOUDY CIRCULATION PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA111 |  | TM140321PC136 | TM140321PT136 | TM140321PT136.MV | YANKEE-TRIM PULPER & OVER FLOW PUMP WHITE WATER PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 |  |  | TM140321HS137 | TM140321SV137 | TM140321SV137 | PULP FROM RECOVERED STOCK CHEST ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBS101 |  | TM140321HS137 | TM140321SV137.ZSC | TM140321SV137.GSC | PULP FROM RECOVERED STOCK CHEST ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBS101 |  | TM140321HS137 | TM140321SV137.ZSO | TM140321SV137.GSO | PULP FROM RECOVERED STOCK CHEST ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBS101 |  | TM140321HS137 | TM140321EV137 | TM140321EV137 | PULP FROM RECOVERED STOCK CHEST ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 |  |  | TM140321NC138 | TM140321NE138 |  | REC PULP CHEST PUMP OUTLET CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230 VAC | [24 empty] | B
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA101 |  | TM140321NC138 | TM140321NT138 | TM140321NT138.MV | REC PULP CHEST PUMP OUTLET CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 6 | %C | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBD101 |  | TM140321NC138 | TM140321NS138 | TM140321NS138.MV | REC PULP CHEST PUMP OUTLET CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA101 | TM1403ASD101 | TM140321NC138 | TM140321NV138 | TM140321NV138.OUT | REC PULP CHEST PUMP OUTLET CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA101 |  | TM140321PC140 | TM140321PT140 | TM140321PT140.MV | PMP DEMAND & CLEANING PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA101 |  | TM140321PC141 | TM140321PT141 | TM140321PT141.MV | SCWW HP SHOWER PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 40 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA111 |  | TM140421FI144 | TM140421FT144 | TM140421FT144.MV | WASTE WATER FROM TM14.3 FLOW | FT | Open channel flow transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 250 | m3/hr | [19 empty] | 4
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM1403JBA101 |  | TM140321PC146 | TM140321PT146 | TM140321PT146.MV | DUST SCWW PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 40 | Bar.g | [19 empty] | 4
VACUUM SYSTEM
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323LC014 | TM140323LT014 | TM110123LT014.MV | VACUUM WW TANK LEVEL | LT | DP Level Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 2500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 | TM1403ASD103 | TM140323LC014 | TM140323LV014 | TM140323LV014.OUT | VACUUM WW TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 | TM1403ASD103 | TM140323HC015 | TM140323HV015 | TM140323HV015.OUT | COOLING TOWER OUTLET BYPASS CV SETPOINT | HV | Control Valve | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBD102 |  | TM140323PS021 | TM140323PS021 | TM140323PS021.L | VACUUM PUMP 1 GEAR REDUCER LUBRICATION OIL PRESSURE | PS | Pressure switch | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBD102 |  | TM140323PS022 | TM140323PS022 | TM140323PS022.L | VACUUM PUMP 2 GEAR REDUCER LUBRICATION OIL PRESSURE | PS | Pressure switch | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323FI065 | TM140323FE065 |  | MAKE-UP WATER VACUUM SYSTEM FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323FI065 | TM140323FT065 | TM140323FT065.MV | MAKE-UP WATER VACUUM SYSTEM FLOW | FT | Magnetic flow transmitter | Field | DCS |  | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 720 | l / min | [19 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323TI066 | TM140323TE066 |  | COOLED SEAL WATER TEMPERATURE | TE | Temperature sensor | Field | [28 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323TI066 | TM140323TT066 | TM140323TT066.MV | COOLED SEAL WATER TEMPERATURE | TT | Temperature transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [19 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323PC067 | TM140323PT067 | TM140323PT067.MV | SEAL WATER TO VACUUM PUMPS PRESSURE | PT | Pressure Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 4 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 | TM1403ASD103 | TM140323PC067 | TM140323PV067 | TM140323PV067.OUT | SEAL WATER TO VACUUM PUMPS PRESSURE CV SETPOINT | PV | Control Valve | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323PI073 | TM140323PT073 | TM140323PT073.MV | VACUUM PUMP 1 PRESSURE | PT | Pressure Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323PI074 | TM140323PT074 | TM140323PT074.MV | VACUUM PUMP 1 PRESSURE | PT | Pressure Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323PI075 | TM140323PT075 | TM140323PT075.MV | VACUUM PUMP 2 PRESSURE | PT | Pressure Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323PI076 | TM140323PT076 | TM140323PT076.MV | VACUUM PUMP 2 PRESSURE | PT | Pressure Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323TI079 | TM140323TE079 |  | COOLING TOWER PUMP 2 OUTLET TEMPERATURE | TE | Temperature sensor | Field | [28 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323TI079 | TM140323TT079 | TM140323TT079.MV | COOLING TOWER PUMP 2 OUTLET TEMPERATURE | TT | Temperature transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [19 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323HS081 | TM140323SV081 | TM140323SV081 | VACUUM PUMP 1 DRAIN ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS081 | TM140323SV081.ZSC | TM140323SV081.GSC | VACUUM PUMP 1 DRAIN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS081 | TM140323SV081.ZSO | TM140323SV081.GSO | VACUUM PUMP 1 DRAIN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS081 | TM140323EV081 | TM140323EV081 | VACUUM PUMP 1 DRAIN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323HS083 | TM140323SV083 | TM140323SV083 | VACUUM PUMP 2 DRAIN ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS083 | TM140323SV083.ZSC | TM140323SV083.GSC | VACUUM PUMP 2 DRAIN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS083 | TM140323SV083.ZSO | TM140323SV083.GSO | VACUUM PUMP 2 DRAIN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS083 | TM140323EV083 | TM140323EV083 | VACUUM PUMP 2 DRAIN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323HS091 | TM140323SV091 | TM140323SV091 | VACUUM PUMP 1 COOLING WATER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS091 | TM140323SV091.ZSC | TM140323SV091.GSC | VACUUM PUMP 1 COOLING WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS091 | TM140323SV091.ZSO | TM140323SV091.GSO | VACUUM PUMP 1 COOLING WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS091 | TM140323EV091 | TM140323EV091 | VACUUM PUMP 1 COOLING WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323FI092 | TM140323FE092 |  | COOLING WATER TO VACUUM PUMP 1 FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323FI092 | TM140323FT092 | TM140323FT092.MV | COOLING WATER TO VACUUM PUMP 1 FLOW | FT | Magnetic flow transmitter | Field | DCS |  | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 430 | l / min | [19 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323HS093 | TM140323SV093 | TM140323SV093 | VACUUM PUMP 2 COOLING WATER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS093 | TM140323SV093.ZSC | TM140323SV093.GSC | VACUUM PUMP 2 COOLING WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS093 | TM140323SV093.ZSO | TM140323SV093.GSO | VACUUM PUMP 2 COOLING WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS093 | TM140323EV093 | TM140323EV093 | VACUUM PUMP 2 COOLING WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323FI094 | TM140323FE094 |  | COOLING WATER TO VACUUM PUMP 2 FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323FI094 | TM140323FT094 | TM140323FT094.MV | COOLING WATER TO VACUUM PUMP 2 FLOW | FT | Magnetic flow transmitter | Field | DCS |  | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 420 | l / min | [19 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323LIS095 | TM140323LT095 | TM140323LT095.MV | VACUUM W.W PIT LEVEL | LT | Radar Level Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | mm |  | 10% | 15% | [16 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 | TM1403ASD103 | TM140323HC096 | TM140323HV096 | TM140323HV096.OUT | COOLING TOWER PUMP OUTLET TO COOLING TOWER CV SETPOINT | HV | Control Valve | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 | TM1403ASD103 | TM140323HC097 | TM140323HV097 | TM140323HV097.OUT | COOLING TOWER PUMP OUTLET TO WIRE WHITE WATER TANK CV SETPOINT | HV | Control Valve | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323HS101 | TM140323SV101 | TM140323SV101 | VACUUM SHEAVE ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS101 | TM140323SV101.ZSC | TM140323SV101.GSC | VACUUM SHEAVE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS101 | TM140323SV101.ZSO | TM140323SV101.GSO | VACUUM SHEAVE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS101 | TM140323EV101 | TM140323EV101 | VACUUM SHEAVE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323PI110 | TM140323PT110 | TM140323PT110.MV | VACUUM PUMP INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 3 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323HC113 | TM140323HV113 | TM140323HV113.OUT | ANTI-SURGE ELECTRIC BUTTERFLY VALVE FEEDBACK | HV | Control Valve | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323HC113 | TM140323HV113 | TM140323HV113.OUT | ANTI-SURGE ELECTRIC BUTTERFLY VALVE CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323LIC114 | TM140323LT114 | TM140323LT114.MV | VACUUM SEPARATOR LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3005 | TM140321 | TM1403JBA101 | TM1403ASD103 | TM140323LIC114 | TM140323LV114 | TM140323LV114.OUT | VACUUM SEPARATOR LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323TISA121 | TM140323TE121 |  | FRONT BEARING TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323TISA121 | TM140323TT121 | TM140323TT121.MV | FRONT BEARING TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323TISA122 | TM140323TE122 |  | REAR BEARING TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323TISA122 | TM140323TT122 | TM140323TT122.MV | REAR BEARING TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323TISA123 | TM140323TE123 |  | THRUST BEARING TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323TISA123 | TM140323TT123 | TM140323TT123.MV | THRUST BEARING TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323TISA124 | TM140323TE124 |  | TEMPERATURE OF STATOR WINDING U | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323TISA124 | TM140323TT124 | TM140323TT124.MV | TEMPERATURE OF STATOR WINDING U | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323TISA125 | TM140323TE125 |  | TEMPERATURE OF STATOR WINDING V | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323TISA125 | TM140323TT125 | TM140323TT125.MV | TEMPERATURE OF STATOR WINDING V | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323TISA126 | TM140323TE126 |  | TEMPERATURE OF STATOR WINDING W | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323TISA126 | TM140323TT126 | TM140323TT126.MV | TEMPERATURE OF STATOR WINDING W | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323XISA127 | TM140323XT127 |  | THE OUTPUT SHAFT VIBRATES IN THE X DIRECTION | XT | Vibration sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323XISA127 | TM140323XT127 | TM140323XT127.MV | THE OUTPUT SHAFT VIBRATES IN THE X DIRECTION | XT | Vibration transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | mm | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323XISA128 | TM140323XT128 |  | THE OUTPUT SHAFT VIBRATES IN THE Y DIRECTION | XT | Vibration sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323XISA128 | TM140323XT128 | TM140323XT128.MV | THE OUTPUT SHAFT VIBRATES IN THE Y DIRECTION | XT | Vibration transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | mm | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323TISA131 | TM140323TE131 |  | OIL SUPPLY OIL TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323TISA131 | TM140323TT131 | TM140323TT131.MV | OIL SUPPLY OIL TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323TISA132 | TM140323TE132 |  | TANK OIL TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323TISA132 | TM140323TT132 | TM140323TT132.MV | TANK OIL TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323PC133 | TM140323PT133 | TM140323PT133.MV | OIL SUPPLY PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 16 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA202 |  | TM140323PC141 | TM140323PT141 | TM140323PT141.MV | UHLE BOX PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 | TM1403ASD103 | TM140323PC141 | TM140323PV141 | TM140323PV141.OUT | UHLE BOX PRESSURE CV SETPOINT | PV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA202 |  | TM140323PI142 | TM140323PT142 | TM140323PT142.MV | PICK-UP BOX PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA202 |  | TM140323PC143 | TM140323PT143 | TM140323PT143.MV | SUCTION PRESS ROLL PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 | TM1403ASD103 | TM140323PC143 | TM140323PV143 | TM140323PV143.OUT | SUCTION PRESS ROLL PRESSURE CV SETPOINT | PV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323HS144 | TM140323SV144 | TM140323SV144 | VACUUM SHEAVE ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS144 | TM140323SV144.ZSC | TM140323SV144.GSC | VACUUM SHEAVE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS144 | TM140323SV144.ZSO | TM140323SV144.GSO | VACUUM SHEAVE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS144 | TM140323EV144 | TM140323EV144 | VACUUM SHEAVE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323HS145 | TM140323SV145 | TM140323SV145 | VACUUM SHEAVE ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS145 | TM140323SV145.ZSC | TM140323SV145.GSC | VACUUM SHEAVE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS145 | TM140323SV145.ZSO | TM140323SV145.GSO | VACUUM SHEAVE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS145 | TM140323EV145 | TM140323EV145 | VACUUM SHEAVE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 |  |  | TM140323HS146 | TM140323SV146 | TM140323SV146 | VACUUM SHEAVE ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323HS146 | TM140323SV146.ZSC | TM140323SV146.GSC | VACUUM SHEAVE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS146 | TM140323SV146.ZSO | TM140323SV146.GSO | VACUUM SHEAVE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBS102 |  | TM140323HS146 | TM140323EV146 | TM140323EV146 | VACUUM SHEAVE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-3703 | TM140323 | TM1403JBA103 |  | TM140323LC147 | TM140323LT147 | TM140323LT147.MV | VACUUM SEPARATOR LEVEL | LT | DP Level Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3000 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 4 | Cutes
SHOWERS SYSTEM
P-OKITM07-10-320-07-PID-3704 | TM140321 |  |  | TM140321HS095 | TM140321SV095 | TM140321SV095 | WIRE CLEANING (FW2) SHOWER WATER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3704 | TM140321 | TM1403JBS205 |  | TM140321HS095 | TM140321SV095.ZSC | TM140321SV095.GSC | WIRE CLEANING (FW2) SHOWER WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3704 | TM140321 | TM1403JBS205 |  | TM140321HS095 | TM140321SV095.ZSO | TM140321SV095.GSO | WIRE CLEANING (FW2) SHOWER WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3704 | TM140321 | TM1403JBS205 |  | TM140321HS095 | TM140321EV095 | TM140321EV095 | WIRE CLEANING (FW2) SHOWER WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3704 | TM140321 |  |  | TM140321HS096 | TM140321SV096 | TM140321SV096 | SHEET SIDE FELT CLEANING(PW5) SHOWER WATER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-3704 | TM140321 | TM1403JBS205 |  | TM140321HS096 | TM140321SV096.ZSC | TM140321SV096.GSC | SHEET SIDE FELT CLEANING(PW5) SHOWER WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3704 | TM140321 | TM1403JBS205 |  | TM140321HS096 | TM140321SV096.ZSO | TM140321SV096.GSO | SHEET SIDE FELT CLEANING(PW5) SHOWER WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3704 | TM140321 | TM1403JBS205 |  | TM140321HS096 | TM140321EV096 | TM140321EV096 | SHEET SIDE FELT CLEANING(PW5) SHOWER WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3704 | TM140321 |  |  | TM140321HS097 | TM140321SV097 | TM140321SV097 | FLOODED NIP (PW7) SHOWER WATER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 0
P-OKITM07-10-320-07-PID-3704 | TM140321 | TM1403JBS205 |  | TM140321HS097 | TM140321SV097.ZSC | TM140321SV097.GSC | FLOODED NIP (PW7) SHOWER WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3704 | TM140321 | TM1403JBS205 |  | TM140321HS097 | TM140321SV097.ZSO | TM140321SV097.GSO | FLOODED NIP (PW7) SHOWER WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3704 | TM140321 | TM1403JBS205 |  | TM140321HS097 | TM140321EV097 | TM140321EV097 | FLOODED NIP (PW7) SHOWER WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3704 | TM140321 |  |  | TM140321HS098 | TM140321SV098 | TM140321SV098 | TAIL CUTTER (PW3) SHOWER WATER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 0
P-OKITM07-10-320-07-PID-3704 | TM140321 | TM1403JBS205 |  | TM140321HS098 | TM140321SV098.ZSC | TM140321SV098.GSC | TAIL CUTTER (PW3) SHOWER WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3704 | TM140321 | TM1403JBS205 |  | TM140321HS098 | TM140321SV098.ZSO | TM140321SV098.GSO | TAIL CUTTER (PW3) SHOWER WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3704 | TM140321 | TM1403JBS205 |  | TM140321HS098 | TM140321EV098 | TM140321EV098 | TAIL CUTTER (PW3) SHOWER WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
FRESH WATER
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM1403JBA102 |  | TM140322LC002 | TM140322LT002 | TM140322LT002.MV | WARM WATER TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3300 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM1403JBA102 | TM1403ASD102 | TM140322LC002 | TM140322LV002 | TM140322LV002.OUT | WARM WATER TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3709 | TM140322 |  |  | TM140322TC004 | TM140322TE004 |  | WARM WATER TANK TEMPERATURE TEMPERATURE | TE | Temperature Sensor | Field
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM1403JBA102 |  | TM140322TC004 | TM140322TT004 | TM140322TT004.MV | WARM WATER TANK TEMPERATURE TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [19 empty] | 1
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM1403JBA102 | TM1403ASD102 | TM140322TC004 | TM140322TV004 | TM140322TV004.OUT | WARM WATER TANK TEMPERATURE TEMPERATURE CV SETPOINT | TV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM1403JBA102 |  | TM140322PC008 | TM140322PT008 | TM140322PT008.MV | FELT HP SHOWER PUMP 1 OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 7 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM1403JBA102 |  | TM140322PC009 | TM140322PT009 | TM140322PT009.MV | FELT HP SHOWER PUMP 2 OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 40 | Bar.g | [19 empty] | 1
COMPRESSED AIR
P-OKITM07-10-320-07-PID-3708 | TM140301 | TM1403JBA112 |  | TM140301PI002 | TM140301PT002 | TM140301PT002.MV | MILL COMPRESSED AIR PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3708 | TM140301 |  |  | TM140301HS003 | TM140301SV003 | TM140301SV003 | COMPRESSED AIR TO TM14.3 ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-3708 | TM140301 | TM1403JBS112 |  | TM140301HS003 | TM140301SV003.ZSC | TM140301SV003.GSC | COMPRESSED AIR TO TM14.3 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3708 | TM140301 | TM1403JBS112 |  | TM140301HS003 | TM140301SV003.ZSO | TM140301SV003.GSO | COMPRESSED AIR TO TM14.3 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3708 | TM140301 | TM1403JBS112 |  | TM140301HS003 | TM140301EV003 | TM140301EV003 | COMPRESSED AIR TO TM14.3 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-3708 | TM140301 | TM1403JBA112 |  | TM140301PI004 | TM140301PT004 | TM140301PT004.MV | INSTRUMENT AIR STORAGE TANK #1 PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3708 | TM140301 |  |  | TM140301HS005 | TM140301SV005 | TM140301SV005 | INSTRUMENT AIR STORAGE TANK #1 DRAIN ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-3708 | TM140301 | TM1403JBS112 |  | TM140301HS005 | TM140301SV005.ZSC | TM140301SV005.GSC | INSTRUMENT AIR STORAGE TANK #1 DRAIN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3708 | TM140301 | TM1403JBS112 |  | TM140301HS005 | TM140301SV005.ZSO | TM140301SV005.GSO | INSTRUMENT AIR STORAGE TANK #1 DRAIN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3708 | TM140301 | TM1403JBS112 |  | TM140301HS005 | TM140301EV005 | TM140301EV005 | INSTRUMENT AIR STORAGE TANK #1 DRAIN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
NaOH SYSTEM
P-OKITM07-10-320-07-PID-3710 | TM140315 |  |  | TM140315HS013 | TM140315SV013 | TM140315SV013 | 32% NaOH TO TM14.3 ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3710 | TM140315 | TM1403JBS205 |  | TM140315HS013 | TM140315SV013.ZSC | TM140315SV013.GSC | 32% NaOH TO TM14.3 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3710 | TM140315 | TM1403JBS205 |  | TM140315HS013 | TM140315SV013.ZSO | TM140315SV013.GSO | 32% NaOH TO TM14.3 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3710 | TM140315 | TM1403JBS205 |  | TM140315HS013 | TM140315EV013 | TM140315EV013 | 32% NaOH TO TM14.3 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
YANKEE COATING
P-OKITM07-10-320-07-PID-3707 | TM140316 | Supplier JB |  | TM140316FC001 | TM140316FE001 |  | RELEASE AGENT PUMP 1 OUTLET FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3707 | TM140316 | Supplier JB |  | TM140316FC001 | TM140316FT001 | TM140316FT001.MV | RELEASE AGENT PUMP 1 OUTLET FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR |  |  | l / min | [19 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3707 | TM140316 | Supplier JB |  | TM140316FI003 | TM140316FE003 |  | RELEASE AGENT PUMP 2 OUTLET FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3707 | TM140316 | Supplier JB |  | TM140316FI003 | TM140316FT003 | TM140316FT003.MV | RELEASE AGENT PUMP 2 OUTLET FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR |  |  | l / min | [19 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3707 | TM140316 | Supplier JB |  | TM140316FI005 | TM140316FE005 |  | RELEASE AGENT PUMP 3 OUTLET FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3707 | TM140316 | Supplier JB |  | TM140316FI005 | TM140316FT005 | TM140316FT005.MV | RELEASE AGENT PUMP 3 OUTLET FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR |  |  | l / min | [19 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3707 | TM140316 | Supplier JB |  | TM140316PC007 | TM140316PT007 | TM140316PT007.MV | YANKEE COATING PUMP 1&2 OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 |  | Bar.g | [19 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3707 | TM140316 | Supplier JB |  | TM140316FI010 | TM140316FE010 |  | YANKEE COATING PUMP 1&2 OUTLET FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3707 | TM140316 | Supplier JB |  | TM140316FI010 | TM140316FT010 | TM140316FT010.MV | YANKEE COATING PUMP 1&2 OUTLET FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR |  |  | l / min | [19 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-3707 | TM140316 | Supplier JB |  | TM140316LI021 | TM140316LI021 | TM140316LI021.MV | COATING TANK LEVEL | LI | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 |  | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 3 |  | HOLD,not finalised
P-OKITM07-10-320-07-PID-3707 | TM140316 | Supplier JB |  | TM140316LI022 | TM140316LI022 | TM140316LI022.MV | RELEASE TANK LEVEL | LI | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 |  | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 3 |  | HOLD,not finalised
P-OKITM07-10-320-07-PID-3707 | TM140316 | Supplier JB |  | TM140316LI023 | TM140316LI023 | TM140316LI023.MV | MAP TANK LEVEL | LI | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 |  | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 3 |  | HOLD,not finalised
STEAM AND CONDENSATE SYSTEM
P-OKITM07-10-320-07-PID-3006 | TM140335 |  |  | TM140335TI001 | TM140335TE001 |  | TO YANKEE 13.5BAR STEAM TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 3 | PMP | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140335 | TM1403JBA112 |  | TM140335TI001 | TM140335TT001 | TM140335TT001.MV | TO YANKEE 13.5BAR STEAM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 350 | ˚C | [19 empty] | 3 | PMP | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140335 | TM1403JBA112 |  | TM140335PI002 | TM140335PT002 | TM140335PT002.MV | TO YANKEE 13.5BAR STEAM PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 15 | Bar.g | [19 empty] | 3 | PMP | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140335 | TM1403JBA112 |  | TM140335FI003 | TM140335FT003 | TM140335FT003.MV | TO YANKEE 13.5BAR STEAM FLOW | FT | Vortex Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 11 | t/h | [19 empty] | 3 | PMP | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140335 |  |  | TM140335TI015 | TM140335TE015 |  | TO YANKEE 20BAR STEAM TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 3 |  | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140335 | TM1403JBA112 |  | TM140335TI015 | TM140335TT015 | TM140335TT015.MV | TO YANKEE 20BAR STEAM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 3 |  | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140335 | TM1403JBA112 |  | TM140335PI016 | TM140335PT016 | TM140335PT016.MV | TO YANKEE 20BAR STEAM PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 25 | Bar.g | [19 empty] | 3 |  | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140335 | TM1403JBA112 |  | TM140335FI017 | TM140335FT017 | TM140335FT017.MV | TO YANKEE 20BAR STEAM FLOW | FT | Vortex Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6.5 | t/h | [19 empty] | 3 |  | Already In PMP IO List
Hall ventilation
P-OKITM07-10-320-08-FLD-3702 | TM140300 | TM1403JBD202 |  | TM140300PDS102 | TM140300PDS102 | TM140300PDS102.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 1
P-OKITM07-10-320-08-FLD-3702 | TM140300 | TM1403JBD202 |  | TM140300PDS103 | TM140300PDS103 | TM140300PDS103.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 1
P-OKITM07-10-320-08-FLD-3702 | TM140300 | TM1403JBD301 |  | TM140300PDS104 | TM140300PDS104 | TM140300PDS104.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 1
P-OKITM07-10-320-08-FLD-3702 | TM140300 | TM1403JBD301 |  | TM140300PDS105 | TM140300PDS105 | TM140300PDS105.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 1
P-OKITM07-10-320-08-FLD-3702 | TM140300 | TM1403JBD301 |  | TM140300PDS106 | TM140300PDS106 | TM140300PDS106.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 1
P-OKITM07-10-320-08-FLD-3702 | TM140300 | TM1403JBD301 |  | TM140300XS107 | TM140300XS107 | TM140300XS107 | TM 14.3 EXHAUST AIR FAN1 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3702 | TM140300 | TM1403JBD301 |  | TM140300XS108 | TM140300XS108 | TM140300XS108 | TM 14.3 EXHAUST AIR FAN2 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3702 | TM140300 | TM1403JBD301 |  | TM140300XS109 | TM140300XS109 | TM140300XS109 | TM 14.3 EXHAUST AIR FAN3 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3702 | TM140300 | TM1403JBD301 |  | TM140300XS110 | TM140300XS110 | TM140300XS110 | TM 14.3 EXHAUST AIR FAN4 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3702 | TM140300 | TM1403JBD301 |  | TM140300XS111 | TM140300XS111 | TM140300XS111 | TM 14.3 EXHAUST AIR FAN5 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3702 | TM140300 | TM1403JBD301 |  | TM140300XS112 | TM140300XS112 | TM140300XS112 | TM 14.3 EXHAUST AIR FAN6 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
HVAC Air Condition
P-OKITM07-10-320-08-FLD-3701 | TM140300 | NA |  | TM140300PDS001 | TM140300PDS001 | TM140300PDS001.L | TM 14.3 TM MCC ROOM AIR FAN FILTER 1 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3701 | TM140300 | NA |  | TM140300PDS002 | TM140300PDS002 | TM140300PDS002.L | TM 14.3 TM MCC ROOM AIR FAN FILTER 2 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3701 | TM140300 | NA |  | TM140300PDS003 | TM140300PDS003 | TM140300PDS003.L | TM 14.3 TM MCC ROOM AIR FAN FILTER 3 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3701 | TM140300 | NA |  | TM140300PDS004 | TM140300PDS004 | TM140300PDS004.L | TM 14.3 TM MCC ROOM AIR FAN FILTER 4 DIFFERENTIAL PRESSURE(MAU1) | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3701 | TM140300 | NA |  | TM140300PDS005 | TM140300PDS005 | TM140300PDS005.L | TM 14.3 TM MCC ROOM AIR FAN FILTER 4 DIFFERENTIAL PRESSURE(MAU2) | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3701 | TM140300 | NA |  | TM140300XS006 | TM140300XS006 | TM140300XS006 | TM 14.3 TM MCC ROOM AC1 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3701 | TM140300 | NA |  | TM140300XS007 | TM140300XS007 | TM140300XS007 | TM 14.3 TM MCC ROOM AC2 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3701 | TM140300 | NA |  | TM140300XS008 | TM140300XS008 | TM140300XS008 | TM 14.3 TM MCC ROOM AC3 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3701 | TM140300 | NA |  | TM140300XS009 | TM140300XS009 | TM140300XS009 | TM 14.3 TM MCC ROOM AC4 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3701 | TM140300 | NA |  | TM140300II010 | TM140300IT010 | TM140300IT010.MV | TM 14.3 TM MCC ROOM AC PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3701 | TM140300 | NA |  | TM140300II011 | TM140300IT011 | TM140300IT011.MV | TM 14.3 SUPPLY FAN PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3701 | TM140300 | NA |  | TM140300II012 | TM140300IT012 | TM140300IT012.MV | TM 14.3 EXHAUST FAN PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3701 | TM140300 | NA |  | TM140300TI011 | TM140300TT011 | TM140300TT011.MV | TM 14.3 TM MCC ROOM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 0 | 50 | ˚C
P-OKITM07-10-320-08-FLD-3701 | TM140300 | NA |  | TM140300MI012 | TM140300MT012 | TM140300MT012.MV | TM 14.3 TM MCC ROOM HUMIDITY | MT | Humidity Transmitter(Integrated In TT) | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 40 | 60 | %
P-OKITM07-10-320-08-FLD-3701 | TM140300 | NA |  | TM140300TI013 | TM140300TT013 | TM140300TT013.MV | TM 14.3 TM RACK ROOM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 0 | 50 | ˚C
P-OKITM07-10-320-08-FLD-3701 | TM140300 | NA |  | TM140300MI014 | TM140300MT014 | TM140300MT014.MV | TM 14.3 TM RACK ROOM HUMIDITY | MT | Humidity Transmitter(Integrated In TT) | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 40 | 60 | %

## 14.3-Exchange Communication LST
PMT: |  |  |  |  | Design Institute: |  |  | Project No. | P-OKITM07-10 | [6 empty] | EXCHANGE COMMUNICTION LIST
[8 empty] | Project Name | DETAIL ENGINEERING FOR 4(FOUR) UNITS TISSUE MACHINE
[8 empty] | Doc. No. | P-OKITM07-10-320-06-LST-3705 | [7 empty] | Abbreviations
Owner: | [7 empty] | Rev. No. | 4 |  |  | Prep'd by | Dengzuijie |  |  |  | EER Electronic Equipment Room |  |  |  | SQRT Square Root
[8 empty] | Purpose | Final |  |  | Chk'd by | Chengjianguo |  |  |  | CCR Control Center Room
[8 empty] | Date | 8,30,2021 |  |  | Appv'd by | LiXiangdong |  |  |  | ESP Electrostatic Precipitator
P&ID No. | Area | Motor Tag reference | Loop No. | Tag No. | System Tag No. | Service Description | Signal Tag | Instrument Type | Location | System | IO Type | Signal |  |  | IO Loc. | PV LO | PV HI | Eng. Unit | Alarm | [6 empty] | State "0" | State "1" | CV Fail Action | CV Ctrl Action | PV CHAR | From |  | Cable |  |  | To |  | Rev. | Supply | Remarks
[12 empty] | Type | Power | Wire |  |  |  |  | LLL | LL | L | Nor. | H | HH | HHH | [5 empty] | JB/Panel No. | TB | Cable Number | Cable Type | Cable Order | Cabinet No. | TB |  | By
MACHINE BROKE
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM140317U003 | TM140317SC025 | TM140317SX025 | TM140317SX025.PRO | BROKE INTERIM TOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM140317U001 | TM140317SC050 | TM140317SX050 | TM140317SX050.PRO | BROKE DEFLAKED CHEST PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM140317A004 | TM140317SC054 | TM140317SX054 | TM140317SX054.PRO | YANKEE PULPER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 2
P-OKITM07-10-320-07-PID-3702 | TM140317 | TM140317U002 | TM140317SC092 | TM140317SX092 | TM140317SX092.PRO | BROKE THICKENER TANK PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
STOCK APPROACH
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320U001 | TM140320SC013 | TM140320SX013 | TM140320SX013.PRO | MIXING CHEST PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320M001 | TM140320EC033 | TM140320SX013 | TM140320SX013.PRO | TICKLER REFINER POWER VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320U003 | TM140320SC046 | TM140320SX046 | TM140320SX046.PRO | SWEETENER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320U004 | TM140320SC056 | TM140320SX056 | TM140320SX056.PRO | MACHINE CHEST PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320U006 | TM140320SC071 | TM140320SX071 | TM140320SX071.PRO | FAN PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3701 | TM140320 | TM140320U007 | TM140320SC102 | TM140320SX102 | TM140320SX102.PRO | W.W OVERFLOW CHEST PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3701 | TM140315 |  | TM140315FC005 | TM140315FX005A | TM140315FX005A.PRO | WET STRENGHT AGENT TO MIXING CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3701 | TM140315 |  | TM140315FC005 | TM140315FX005B | TM140315FX005B.PRO | WET STRENGHT AGENT TO MIXING CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3701 | TM140315 |  | TM140315FC006 | TM140315FX006A | TM140315FX006A.PRO | DRY STRENGHT AGENT TO MACHINE CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3701 | TM140315 |  | TM140315FC006 | TM140315FX006B | TM140315FX006B.PRO | DRY STRENGHT AGENT TO MACHINE CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3701 | TM140315 |  | TM140315FC007 | TM140315FX007A | TM140315FX007A.PRO | SOFT AGENT TO MIXING CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3701 | TM140315 |  | TM140315FC007 | TM140315FX007B | TM140315FX007B.PRO | SOFT AGENT TO MIXING CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3701 | TM140315 |  | TM140315FC008 | TM140315FX008A | TM140315FX008A.PRO | CMC TO FAN PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-3701 | TM140315 |  | TM140315FC008 | TM140315FX008B | TM140315FX008B.PRO | CMC TO FAN PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
WHITE WATER AND FIBRE RECOVERY
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321M001 | TM140321SC027 | TM140321SX027 | TM140321SX027.PRO | DISC FILTER MOTOR SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321U001 | TM140321SC029 | TM140321SX029 | TM140321SX029.PRO | DISC FILTER FEED PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321U002 | TM140321SC030 | TM140321SX030 | TM140321SX030.PRO | TM AREA CRC PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321U003 | TM140321SC031 | TM140321SX031 | TM140321SX031.PRO | YANKEE-TRIM PULPER & OVER FLOW PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321U007 | TM140321SC032 | TM140321SX032 | TM140321SX032.PRO | CLARIFIED TANK PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321U008 | TM140321SC033 | TM140321SX033 | TM140321SX033.PRO | DISC FILTER SHOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321U004 | TM140321SC047 | TM140321SX047 | TM140321SX047.PRO | REC PULP CHEST PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321U009 | TM140321SC048 | TM140321SX048 | TM140321SX048.PRO | CWW LP SHOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321U006 | TM140321SC049 | TM140321SX049 | TM140321SX049.PRO | CWW HP SHOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321U005 | TM140321SC051 | TM140321SX051 | TM140321SX051.PRO | CLOUDY CIRCULATION PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321U011 | TM140321SC052 | TM140321SX052 | TM140321SX052.PRO | SCWW LP SHOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321U013 | TM140321SC142 | TM140321SX142 | TM140321SX142.PRO | SCWW HP SHOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3705 | TM140321 | TM140321U012 | TM140321SC143 | TM140321SX143 | TM140321SX143.PRO | PMP DEMAND & CLEANING PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3705 | TM140121 | TM140321U014 | TM140121SC146 | TM140121SX146 | TM140121SX146.PRO | DUST SCWW PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
FRESH WATER
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM140322U008 | TM140322SC031 | TM140322SX031 | TM140322SX031.PRO | WARM WATER PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM140322U009 | TM140322SC032 | TM140322SX032 | TM140322SX032.PRO | WARM WATER PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM140322U010 | TM140322SC033 | TM140322SX033 | TM140322SX033.PRO | FELT HP SHOWER PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3709 | TM140322 | TM140322U011 | TM140322SC034 | TM140322SX034 | TM140322SX034.PRO | FELT HP SHOWER PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
YANKEE COATING
P-OKITM07-10-320-07-PID-3357 | TM140316 |  | TM140316SC002 | TM140316SX002 | TM140316SX002.PRO | RELEASE AGENT PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3357 | TM140316 |  | TM140316SC004 | TM140316SX004 | TM140316SX004.PRO | RELEASE AGENT PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3357 | TM140316 |  | TM140316SC006 | TM140316SX006 | TM140316SX006.PRO | RELEASE AGENT PUMP 3 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3357 | TM140316 |  | TM140316SC008 | TM140316SX008 | TM140316SX008.PRO | YANKEE COATING PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3357 | TM140316 |  | TM140316SC009 | TM140316SX009 | TM140316SX009.PRO | YANKEE COATING PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B

## IO Summary
I/O COUNT SUMMARY
| AI | AO | DI | DO | TOTAL | REMARK
DCS | 118 | 45 | 195 | 78 | 436 | TM14.3 DCS
SIS | 0 | 0 | 0 | 0 | 0
SUM | 118 | 45 | 195 | 78 | 436

## Definitions
P&ID No. | The P&ID drawing number where the equipment is located.
Area | The Area where the equipment is located
Loop No. | Loop Number
Tag No. | Tag Name according to APP guideline
System Tag No. | Tag name to be appeared in DCS
Service Description | Process/service description
Signal Tag | Signal Tagname
Instrument Type | Type of instrument
Location | Location of the instrument
System | in DCS, PLC or local
IO Type | Type of input or output
Signal - Type | Signal type
Signal - Power | Power for the signal
Signal - Wire | wiring configuration
IO Loc. | Input and Output location
PV LO | Range Low
PV HI | Range High
Eng. Unit | Engineering Unit
Alarm | LLL- Low Low Low, HHH- High High High etc
State "0" | For Valves, If signal is zero, what willl be the valve opening.
State "1" | For Valves, If signal is one, what willl be the valve opening.
CV fail Action | For Valves, If air fails, what willl be the valve status.
CV Control Action | For Valves, Direction of the control.
PV CHAR | Process value characteristics
Rev | Revision
Supply By | Supplier name
Remarks