## 14.4-IO Database
PMT: | [5 empty] | Design Institute: |  |  | Project No. | P-OKITM07-10 | [6 empty] | DCS I/O Database
[9 empty] | Project Name | DETAIL ENGINEERING FOR 4(FOUR) UNITS TISSUE MACHINE
[9 empty] | Doc. No. | P-OKITM07-10-320-06-LST-4005 | [7 empty] | Abbreviations
Owner: | [8 empty] | Rev. No. | 4 |  |  | Prep'd by | Dengzuijie |  |  |  | EER Electronic Equipment Room |  |  |  | SQRT Square Root
[9 empty] | Purpose | Final |  |  | Chk'd by | Chengjianguo |  |  |  | CCR Control Center Room
[9 empty] | Date | 8,30,2021 |  |  | Appv'd by | LiXiangdong |  |  |  | ESP Electrostatic Precipitator
P&ID No. | Area | JB No. | ASD No. | Loop No. | Tag No. | System Tag No. | Service Description | Signal Tag | Instrument Type | Location | System | IO Type | Signal |  |  | IO Loc. | PV LO | PV HI | Eng. Unit | Alarm | [6 empty] | State "0" | State "1" | CV Fail Action | CV Ctrl Action | PV CHAR | From |  | Cable |  |  | To |  | Rev. | Supply | Remarks
[13 empty] | Type | Power | Wire |  |  |  |  | LLL | LL | L | Nor. | H | HH | HHH | [5 empty] | JB/Panel No. | TB | Cable Number | Cable Type | Cable Order | Cabinet No. | TB |  | By
MACHINE BROKE
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD102 |  | TM140417FS001 | TM140417FS001 | TM140417FS001.L | SEALING WATER TO YANKEE PULPER PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD111 |  | TM140417FS002 | TM140417FS002 | TM140417FS002.L | SEALING WATER TO BROKE DEFLAKED CHEST PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1403JBD112 |  | TM140417FS003 | TM140417FS003 | TM140417FS003.L | SEALING WATER TO BROKE INTERIM TOWER PUMP 2 FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS005 | TM140417SV005 | TM140417SV005 | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS103 |  | TM140417HS005 | TM140417SV005.ZSC | TM140417SV005.GSC | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS103 |  | TM140417HS005 | TM140417SV005.ZSO | TM140417SV005.GSO | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS103 |  | TM140417HS005 | TM140417EV005 | TM140417EV005 | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS006 | TM140417SV006 | TM140417SV006 | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS103 |  | TM140417HS006 | TM140417SV006.ZSC | TM140417SV006.GSC | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS103 |  | TM140417HS006 | TM140417SV006.ZSO | TM140417SV006.GSO | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS103 |  | TM140417HS006 | TM140417EV006 | TM140417EV006 | PULP FROM PULPER TO YANKEE PULPER PUMP FLUSHING WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA103 |  | TM140417LC007 | TM140417LT007 | TM140417LT007.MV | YANKEE PULPER LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 5000 | mm |  | 20% | 30% |  | 80% | 90% | [13 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA103 | TM1404ASD104 | TM140417LC007 | TM140417LV007A | TM140417LV007A.OUT | YANKEE PULPER LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA103 | TM1404ASD104 | TM140417LC007 | TM140417LV007B | TM140417LV007B.OUT | YANKEE PULPER LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA103 | TM1404ASD104 | TM140417LC007 | TM140417LV007C | TM140417LV007C.OUT | YANKEE PULPER LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417EC008 | TM140417EX008 | TM140417EX008.SOF | YANKEE PULPER SHEET BREAK | EX | DCS software function | DCS | DCS |  | Software function | [25 empty] | B
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD102 |  | TM140417FS009 | TM140417FS009 | TM140417FS009.L | SEALING WATER TO YANKEE PULPER RECIRCULATION PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD102 |  | TM140417FS010 | TM140417FS010 | TM140417FS010.L | SEALING WATER TO YANKEE PULPER AGITATOR FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS011 | TM140417SV011 | TM140417SV011 | YANKEE PULPER SHOWER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS103 |  | TM140417HS011 | TM140417SV011.ZSC | TM140417SV011.GSC | YANKEE PULPER SHOWER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS103 |  | TM140417HS011 | TM140417SV011.ZSO | TM140417SV011.GSO | YANKEE PULPER SHOWER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS103 |  | TM140417HS011 | TM140417EV011 | TM140417EV011 | YANKEE PULPER SHOWER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417NC012 | TM140417NE012 |  | PULP FROM YANKEE PULPER TO BROKE INTERIM TOWER CONSISTENCY | NE | Blade Consistency Sensor | Field |  |  |  | 230 VAC | [24 empty] | 0
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA103 |  | TM140417NC012 | TM140417NT012 | TM140417NT012.MV | PULP FROM YANKEE PULPER TO BROKE INTERIM TOWER CONSISTENCY | NT | Blade Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 6 | %Cs | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417FC113 | TM140417FE113 |  | DILUTITION WATER TO YANKEE PULPER FLOW | FE | Magnetic Flow Sensor | Field | DCS | [27 empty] | B
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA103 |  | TM140417FC113 | TM140417FT113 | TM140417FT113.MV | DILUTITION WATER TO YANKEE PULPER FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 3500 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA103 | TM1404ASD104 | TM140417FC113 | TM140417FV113 | TM140417FV113.OUT | DILUTITION WATER TO YANKEE PULPER FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1403JBA112 |  | TM140417LI015 | TM140417LT015 | TM140417LT015.MV | BROKE INTERIM TOWER LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 12600 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS016 | TM140417SV016 | TM140417SV016 | PULP FROM BROKE INTERIM TOWER TO BROKE INTERIM TOWER PUMP 2 ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1403JBS113 |  | TM140417HS016 | TM140417SV016.ZSC | TM140417SV016.GSC | PULP FROM BROKE INTERIM TOWER TO BROKE INTERIM TOWER PUMP 2 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1403JBS113 |  | TM140417HS016 | TM140417SV016.ZSO | TM140417SV016.GSO | PULP FROM BROKE INTERIM TOWER TO BROKE INTERIM TOWER PUMP 2 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1403JBS113 |  | TM140417HS016 | TM140417EV016 | TM140417EV016 | PULP FROM BROKE INTERIM TOWER TO BROKE INTERIM TOWER PUMP 2 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1403JBA112 | TM1404ASD113 | TM140417HC017 | TM140417HV017 | TM140417HV017.OUT | BROKE INTERIM TOWER PUMP 1 INLET DILUTION WATER CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS020 | TM140417SV020 | TM140417SV020 | PULP FROM BROKE INTERIM TOWER TO PUMP 1 ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1403JBS113 |  | TM140417HS020 | TM140417SV020.ZSC | TM140417SV020.GSC | PULP FROM BROKE INTERIM TOWER TO PUMP 1 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1403JBS113 |  | TM140417HS020 | TM140417SV020.ZSO | TM140417SV020.GSO | PULP FROM BROKE INTERIM TOWER TO PUMP 1 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1403JBS113 |  | TM140417HS020 | TM140417EV020 | TM140417EV020 | PULP FROM BROKE INTERIM TOWER TO PUMP 1 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS021 | TM140417SV021 | TM140417SV021 | HC-CLEANER FEED ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS201 |  | TM140417HS021 | TM140417SV021.ZSC | TM140417SV021.GSC | HC-CLEANER FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS201 |  | TM140417HS021 | TM140417SV021.ZSO | TM140417SV021.GSO | HC-CLEANER FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS201 |  | TM140417HS021 | TM140417EV021 | TM140417EV021 | HC-CLEANER FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS022 | TM140417SV022 | TM140417SV022 | HC-CLEANER ACCEPT ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS201 |  | TM140417HS022 | TM140417SV022.ZSC | TM140417SV022.GSC | HC-CLEANER ACCEPT ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS201 |  | TM140417HS022 | TM140417SV022.ZSO | TM140417SV022.GSO | HC-CLEANER ACCEPT ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS201 |  | TM140417HS022 | TM140417EV022 | TM140417EV022 | HC-CLEANER ACCEPT ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS023 | TM140417SV023 | TM140417SV023 | HC-CLEANER BYPASS ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS201 |  | TM140417HS023 | TM140417SV023.ZSC | TM140417SV023.GSC | HC-CLEANER BYPASS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS201 |  | TM140417HS023 | TM140417SV023.ZSO | TM140417SV023.GSO | HC-CLEANER BYPASS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS201 |  | TM140417HS023 | TM140417EV023 | TM140417EV023 | HC-CLEANER BYPASS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA201 |  | TM140417PC028 | TM140417PT028 | TM140417PT028.MV | HC-CLEANER FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA201 |  | TM140417PC029 | TM140417PT029 | TM140417PT029.MV | HC-CLEANER ACCEPT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA201 | TM1404ASD201 | TM140417PC029 | TM140417PV029 | TM140417PV029.OUT | HC-CLEANER ACCEPT PRESSURE CV SETPOINT | PV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417KS031 | TM140417KX031 | TM140417KX031.SOF | HC-CLEANER JUNK TRAP SEQUENCE | KX | DCS software function | DCS | DCS |  | Software function
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS031A | TM140417SV031A | TM140417SV031A | HC-CLEANER REJECT TOP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD203 |  | TM140417HS031A | TM140417SV031A.ZSC | TM140417SV031A.GSC | HC-CLEANER REJECT TOP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD203 |  | TM140417HS031A | TM140417SV031A.ZSO | TM140417SV031A.GSO | HC-CLEANER REJECT TOP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD203 | TM1404ASD202 | TM140417HS031A | TM140417EV031A | TM140417EV031A | HC-CLEANER REJECT TOP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS031B | TM140417SV031B | TM140417SV031B | HC-CLEANER REJECT BOTTOM ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD203 |  | TM140417HS031B | TM140417SV031B.ZSC | TM140417SV031B.GSC | HC-CLEANER REJECT BOTTOM ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD203 |  | TM140417HS031B | TM140417SV031B.ZSO | TM140417SV031B.GSO | HC-CLEANER REJECT BOTTOM ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD203 | TM1404ASD202 | TM140417HS031B | TM140417EV031B | TM140417EV031B | HC-CLEANER REJECT BOTTOM ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS031C | TM140417SV031C | TM140417SV031C | HC-CLEANER REJECT TOP FLUSHING ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD203 |  | TM140417HS031C | TM140417SV031C.ZSC | TM140417SV031C.GSC | HC-CLEANER REJECT TOP FLUSHING ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD203 |  | TM140417HS031C | TM140417SV031C.ZSO | TM140417SV031C.GSO | HC-CLEANER REJECT TOP FLUSHING ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD203 | TM1404ASD202 | TM140417HS031C | TM140417EV031C | TM140417EV031C | HC-CLEANER REJECT TOP FLUSHING ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS031D | TM140417SV031D | TM140417SV031D | HC-CLEANER REJECT BOTTOM FLUSHING ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD203 |  | TM140417HS031D | TM140417SV031D.ZSC | TM140417SV031D.GSC | HC-CLEANER REJECT BOTTOM FLUSHING ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD203 |  | TM140417HS031D | TM140417SV031D.ZSO | TM140417SV031D.GSO | HC-CLEANER REJECT BOTTOM FLUSHING ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD203 | TM1404ASD202 | TM140417HS031D | TM140417EV031D | TM140417EV031D | HC-CLEANER REJECT BOTTOM FLUSHING ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS031E | TM140417SV031E | TM140417SV031E | HC-CLEANER REJECT EXHAUSTING ON/OFF VALVE OPENED | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD203 |  | TM140417HS031E | TM140417SV031E.ZSC | TM140417SV031E.GSC | HC-CLEANER REJECT EXHAUSTING ON/OFF VALVE OPENED CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD203 |  | TM140417HS031E | TM140417SV031E.ZSO | TM140417SV031E.GSO | HC-CLEANER REJECT EXHAUSTING ON/OFF VALVE OPENED OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD203 | TM1404ASD202 | TM140417HS031E | TM140417EV031E | TM140417EV031E | HC-CLEANER REJECT EXHAUSTING ON/OFF VALVE OPENED SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA101 |  | TM140417LC032 | TM140417LT032 | TM140417LT032.MV | THICKENER BROKE TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS034 | TM140417SV034 | TM140417SV034 | BROKE DEFLAKER FLUSHING ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS203 |  | TM140417HS034 | TM140417SV034.ZSC | TM140417SV034.GSC | BROKE DEFLAKER FLUSHING ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS203 |  | TM140417HS034 | TM140417SV034.ZSO | TM140417SV034.GSO | BROKE DEFLAKER FLUSHING ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS203 |  | TM140417HS034 | TM140417EV034 | TM140417EV034 | BROKE DEFLAKER FLUSHING ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS035 | TM140417SV035 | TM140417SV035 | BROKE DEFLAKER FEED ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS203 |  | TM140417HS035 | TM140417SV035.ZSC | TM140417SV035.GSC | BROKE DEFLAKER FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS203 |  | TM140417HS035 | TM140417SV035.ZSO | TM140417SV035.GSO | BROKE DEFLAKER FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS203 |  | TM140417HS035 | TM140417EV035 | TM140417EV035 | BROKE DEFLAKER FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS036 | TM140417SV036 | TM140417SV036 | BROKE DEFLAKER ACCEPT ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS203 |  | TM140417HS036 | TM140417SV036.ZSC | TM140417SV036.GSC | BROKE DEFLAKER ACCEPT ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS203 |  | TM140417HS036 | TM140417SV036.ZSO | TM140417SV036.GSO | BROKE DEFLAKER ACCEPT ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS203 |  | TM140417HS036 | TM140417EV036 | TM140417EV036 | BROKE DEFLAKER ACCEPT ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS037 | TM140417SV037 | TM140417SV037 | BROKE DEFLAKER BYPASS ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS203 |  | TM140417HS037 | TM140417SV037.ZSC | TM140417SV037.GSC | BROKE DEFLAKER BYPASS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS203 |  | TM140417HS037 | TM140417SV037.ZSO | TM140417SV037.GSO | BROKE DEFLAKER BYPASS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS203 |  | TM140417HS037 | TM140417EV037 | TM140417EV037 | BROKE DEFLAKER BYPASS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA201 |  | TM140417PI038 | TM140417PT038 | TM140417PT038.MV | BROKE DEFLAKER FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417FC039 | TM140417FE039 |  | STOCK TO BROKE DEFLAKED CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA101 |  | TM140417FC039 | TM140417FT039 | TM140417FT039.MV | STOCK TO BROKE DEFLAKED CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 720 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA101 | TM1404ASD101 | TM140417FC039 | TM140417FV039 | TM140417FV039.OUT | STOCK TO BROKE DEFLAKED CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417WC040 | TM140417WX040 | TM140417WX040.SOF | BROKE DEFLAKER SEC SETPOINT | WX | DCS software function | DCS | DCS |  | Software function
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD201 |  | TM140417FS041 | TM140417FS041 | TM140417FS041.L | SEALING WATER TO BROKE DEFLAKER FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA112 |  | TM140417LC042 | TM140417LT042 | TM140417LT042.MV | BROKE DEFLAKED CHEST LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA112 | TM1404ASD112 | TM140417LC042 | TM140417LV042 | TM140417LV042.OUT | BROKE DEFLAKED CHEST LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417NC044 | TM140417NE044 |  | DEFLAKED BROKE TO MIXING CHEST CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230 VAC | [24 empty] | B
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA112 |  | TM140417NC044 | TM140417NT044 | TM140417NT044.MV | DEFLAKED BROKE TO MIXING CHEST CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 6 | %Cs | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD111 |  | TM140417NC044 | TM140417NS044 | TM140417NS044.MV | DEFLAKED BROKE TO MIXING CHEST CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA112 | TM1404ASD112 | TM140417NC044 | TM140417NV044 | TM140417NV044.OUT | DEFLAKED BROKE TO MIXING CHEST CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS046 | TM140417SV046 | TM140417SV046 | BROKE DEFLAKED CHEST OUTLET ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS112 |  | TM140417HS046 | TM140417SV046.ZSC | TM140417SV046.GSC | BROKE DEFLAKED CHEST OUTLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS112 |  | TM140417HS046 | TM140417SV046.ZSO | TM140417SV046.GSO | BROKE DEFLAKED CHEST OUTLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS112 |  | TM140417HS046 | TM140417EV046 | TM140417EV046 | BROKE DEFLAKED CHEST OUTLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS048 | TM140417SV048 | TM140417SV048 | SEALING WATER TO YANKEE PULPER AGITATOR ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS103 |  | TM140417HS048 | TM140417SV048.ZSC | TM140417SV048.GSC | SEALING WATER TO YANKEE PULPER AGITATOR ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS103 |  | TM140417HS048 | TM140417SV048.ZSO | TM140417SV048.GSO | SEALING WATER TO YANKEE PULPER AGITATOR ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS103 |  | TM140417HS048 | TM140417EV048 | TM140417EV048 | SEALING WATER TO YANKEE PULPER AGITATOR ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA112 |  | TM140417PC049 | TM140417PT049 | TM140417PT049.MV | BROKE DEFLAKED CHEST PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 4 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS051 | TM140417SV051 | TM140417SV051 | SEALING WATER TO BROKE DEFLAKER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS203 |  | TM140417HS051 | TM140417SV051.ZSC | TM140417SV051.GSC | SEALING WATER TO BROKE DEFLAKER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS203 |  | TM140417HS051 | TM140417SV051.ZSO | TM140417SV051.GSO | SEALING WATER TO BROKE DEFLAKER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS203 |  | TM140417HS051 | TM140417EV051 | TM140417EV051 | SEALING WATER TO BROKE DEFLAKER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA201 |  | TM140417PI052 | TM140417PT052 | TM140417PT052.MV | BROKE DEFLAKER ACCEPT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD201 |  | TM140417TS053 | TM140417TS053 | TM140417TS053.H | BROKE DEFLAKER OUTLET TEMPERATURE HIGH | TS | Temperature switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [7 empty] | Temp. High | Not Temp. High | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS055 | TM140417SV055 | TM140417SV055 | SHOWER WATER TO YANKEE PULPER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS103 |  | TM140417HS055 | TM140417SV055.ZSC | TM140417SV055.GSC | SHOWER WATER TO YANKEE PULPER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS103 |  | TM140417HS055 | TM140417SV055.ZSO | TM140417SV055.GSO | SHOWER WATER TO YANKEE PULPER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS103 |  | TM140417HS055 | TM140417EV055 | TM140417EV055 | SHOWER WATER TO YANKEE PULPER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1403JBA112 | TM1404ASD113 | TM140417HC056 | TM140417HV056 | TM140417HV056.OUT | BROKE INTERIM TOWER PUMP OUTLET CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417KS057 | TM140417SV057A | TM140417SV057A | BROKE THICKENER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS201 |  | TM140417KS057 | TM140417SV057A.ZSC | TM140417SV057A.GSC | BROKE THICKENER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS201 |  | TM140417KS057 | TM140417SV057A.ZSO | TM140417SV057A.GSO | BROKE THICKENER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS201 |  | TM140417KS057 | TM140417EV057A | TM140417EV057A | BROKE THICKENER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD201 | TM1404ASD201 | TM140417KS057 | TM140417EV057B | TM140417EV057B | BROKE THICKENER ON/OFF VALVE CLOSED SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD201 | TM1404ASD201 | TM140417KS057 | TM140417EV057C | TM140417EV057C | BROKE THICKENER ON/OFF VALVE OPENED SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417HS058 | TM140417SV058 | TM140417SV058 | BROKE THICKENER TANK PUMP INLET ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS101 |  | TM140417HS058 | TM140417SV058.ZSC | TM140417SV058.GSC | BROKE THICKENER TANK PUMP INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS101 |  | TM140417HS058 | TM140417SV058.ZSO | TM140417SV058.GSO | BROKE THICKENER TANK PUMP INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS101 |  | TM140417HS058 | TM140417EV058 | TM140417EV058 | BROKE THICKENER TANK PUMP INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS112 |  | TM140417HS061 | TM140417SV061 | TM140417SV061 | BROKE DEFLAKED CHEST PUMP OUTLET TO MIXING CHEST ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS112 |  | TM140417HS061 | TM140417SV061.ZSC | TM140417SV061.GSC | BROKE DEFLAKED CHEST PUMP OUTLET TO MIXING CHEST ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS112 |  | TM140417HS061 | TM140417SV061.ZSO | TM140417SV061.GSO | BROKE DEFLAKED CHEST PUMP OUTLET TO MIXING CHEST ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS112 |  | TM140417HS061 | TM140417EV061 | TM140417EV061 | BROKE DEFLAKED CHEST PUMP OUTLET TO MIXING CHEST ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS112 |  | TM140417HS062 | TM140417SV062 | TM140417SV062 | BROKE DEFLAKED CHEST PUMP OUTLET TO BROKE THICKENER TANK ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS112 |  | TM140417HS062 | TM140417SV062.ZSC | TM140417SV062.GSC | BROKE DEFLAKED CHEST PUMP OUTLET TO BROKE THICKENER TANK ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS112 |  | TM140417HS062 | TM140417SV062.ZSO | TM140417SV062.GSO | BROKE DEFLAKED CHEST PUMP OUTLET TO BROKE THICKENER TANK ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBS112 |  | TM140417HS062 | TM140417EV062 | TM140417EV062 | BROKE DEFLAKED CHEST PUMP OUTLET TO BROKE THICKENER TANK ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 |  |  | TM140417NC091 | TM140417NE091 |  | BROKE THICKENER TANK PUMP OUTLET CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230 VAC | [24 empty] | B
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA101 |  | TM140417NC091 | TM140417NT091 | TM140417NT091.MV | BROKE THICKENER TANK PUMP OUTLET CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 6 | %Cs | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD101 |  | TM140417NC091 | TM140417NS091 | TM140417NS091.MV | BROKE THICKENER TANK PUMP OUTLET CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBA101 | TM1404ASD101 | TM140417NC091 | TM140417NV091 | TM140417NV091.OUT | BROKE THICKENER TANK PUMP OUTLET CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD102 |  | TM140417XS093 | TM140417XS093A | TM140417EX008A | SHEET BREAK | XS | Web break signals | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Web break | Not Web break | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD102 |  | TM140417XS093 | TM140417XS093B | TM140417EX008B | SHEET BREAK | XS | Web break signals | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Web break | Not Web break | [10 empty] | 1
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM1404JBD101 |  | TM140417FS095 | TM140417FS095 | TM140417FS095.L | SEALING WATER TO BROKE BROKE THICKENER TANK PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
STOCK APPROACH
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420FC001 | TM140420FE001 |  | NBKP#3 REFINED TOWER #1 PUMP TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS | [27 empty] | B
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 |  | TM140420FC001 | TM140420FT001 | TM140420FT001.MV | NBKP#3 REFINED TOWER #1 PUMP TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1000 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 | TM1404ASD111 | TM140420FC001 | TM140420FV001 | TM140420FV001.OUT | NBKP#3 REFINED TOWER #1 PUMP TO MIXING CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420FC002 | TM140420FE002 |  | LBKP 2 INTERMEDIATE TOWER PUMP TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 |  | TM140420FC002 | TM140420FT002 | TM140420FT002.MV | LBKP 2 INTERMEDIATE TOWER PUMP TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 2700 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 | TM1404ASD111 | TM140420FC002 | TM140420FV002 | TM140420FV002.OUT | LBKP 2 INTERMEDIATE TOWER PUMP TO MIXING CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420FC003 | TM140420FE003 |  | BROKE DEFLAKED CHEST PUMP TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 |  | TM140420FC003 | TM140420FT003 | TM140420FT003.MV | BROKE DEFLAKED CHEST PUMP TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 720 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 | TM1404ASD111 | TM140420FC003 | TM140420FV003 | TM140420FV003.OUT | BROKE DEFLAKED CHEST PUMP TO MIXING CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420FC004 | TM140420FE004 |  | SP2 BROKE TOWER PUMP TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 |  | TM140420FC004 | TM140420FT004 | TM140420FT004.MV | SP2 BROKE TOWER PUMP TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1100 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 | TM1404ASD111 | TM140420FC004 | TM140420FV004 | TM140420FV004.OUT | SP2 BROKE TOWER PUMP TO MIXING CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420FC005 | TM140420FE005 |  | RECOVERED STOCK PUMP TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 |  | TM140420FC005 | TM140420FT005 | TM140420FT005.MV | RECOVERED STOCK PUMP TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1800 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420HS006 | TM140420SV006 | TM140420SV006 | SWEETENER PUMP INLET ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS111 |  | TM140420HS006 | TM140420SV006.ZSC | TM140420SV006.GSC | SWEETENER PUMP INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS111 |  | TM140420HS006 | TM140420SV006.ZSO | TM140420SV006.GSO | SWEETENER PUMP INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS111 |  | TM140420HS006 | TM140420EV006 | TM140420EV006 | SWEETENER PUMP INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 |  | TM140420LC008 | TM140420LT008 | TM140420LT008.MV | MIXING CHEST LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 5000 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420HS009 | TM140420SV009 | TM140420SV009 | DILUTION WATER TO SWEETENER PUMP INLET ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS111 |  | TM140420HS009 | TM140420SV009.ZSC | TM140420SV009.GSC | DILUTION WATER TO SWEETENER PUMP INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS111 |  | TM140420HS009 | TM140420SV009.ZSO | TM140420SV009.GSO | DILUTION WATER TO SWEETENER PUMP INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS111 |  | TM140420HS009 | TM140420EV009 | TM140420EV009 | DILUTION WATER TO SWEETENER PUMP INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD111 |  | TM140420FS010 | TM140420FS010 | TM140420FS010.L | SEALING WATER TO SWEETENER PUMP FLOW | FS | Flow Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420HS011 | TM140420SV011 | TM140420SV011 | MIXING CHEST DISCHAGE ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS111 |  | TM140420HS011 | TM140420SV011.ZSC | TM140420SV011.GSC | MIXING CHEST DISCHAGE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS111 |  | TM140420HS011 | TM140420SV011.ZSO | TM140420SV011.GSO | MIXING CHEST DISCHAGE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS111 |  | TM140420HS011 | TM140420EV011 | TM140420EV011 | MIXING CHEST DISCHAGE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420NC012 | TM140420NE012 |  | MIXING CHEST PUMP OUTLET CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230 VAC | [24 empty] | B
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 |  | TM140420NC012 | TM140420NT012 | TM140420NT012.MV | MIXING CHEST PUMP OUTLET CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 6 | %C | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD111 |  | TM140420NC012 | TM140420NS012 | TM140420NS012.MV | MIXING CHEST PUMP OUTLET CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 | TM1404ASD111 | TM140420NC012 | TM140420NV012 | TM140420NV012.OUT | MIXING CHEST PUMP OUTLET CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD111 |  | TM140420FS014 | TM140420FS014 | TM140420FS014.L | SEALING WATER TO MIXING CHEST PUMP 1 FLOW | FS | Flow Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420FC015 | TM140420FE015 |  | NBKP#3 REFINED TOWER #2 PUMP1 TO MIXING CHEST FLOW | FE | Magnetic Flow Sensor | Field | DCS | [27 empty] | B
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 |  | TM140420FC015 | TM140420FT015 | TM140420FT015.MV | NBKP#3 REFINED TOWER #2 PUMP1 TO MIXING CHEST FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1000 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 | TM1404ASD111 | TM140420FC015 | TM140420FV015 | TM140420FV015.OUT | NBKP#3 REFINED TOWER #2 PUMP1 TO MIXING CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA201 |  | TM140420PI021 | TM140420PT021 | TM140420PT021.MV | TICKLER REFINER FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420CB01 |  | TM140420PI021 | TM140420PI021 | TM140420PI021.IND | TICKLER REFINER FEED PRESSURE | PI | Local digital indicator | Field | DCS | AO | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA201 |  | TM140420PI022 | TM140420PT022 | TM140420PT022.MV | TICKLER REFINER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420CB01 |  | TM140420PI022 | TM140420PI022 | TM140420PI022.IND | TICKLER REFINER OUTLET PRESSURE | PI | Local digital indicator | Field | DCS | AO | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420HS024 | TM140420SV024 | TM140420SV024 | TICKLER REFINER FEED ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS204 |  | TM140420HS024 | TM140420SV024.ZSC | TM140420SV024.GSC | TICKLER REFINER FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS204 |  | TM140420HS024 | TM140420SV024.ZSO | TM140420SV024.GSO | TICKLER REFINER FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS204 |  | TM140420HS024 | TM140420EV024 | TM140420EV024 | TICKLER REFINER FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420HS025 | TM140420SV025 | TM140420SV025 | TICKLER REFINER ACCEPT ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS204 |  | TM140420HS025 | TM140420SV025.ZSC | TM140420SV025.GSC | TICKLER REFINER ACCEPT ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS204 |  | TM140420HS025 | TM140420SV025.ZSO | TM140420SV025.GSO | TICKLER REFINER ACCEPT ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS204 |  | TM140420HS025 | TM140420EV025 | TM140420EV025 | TICKLER REFINER ACCEPT ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420HS026 | TM140420SV026 | TM140420SV026 | TICKLER REFINER BYPASS ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS204 |  | TM140420HS026 | TM140420SV026.ZSC | TM140420SV026.GSC | TICKLER REFINER BYPASS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS204 |  | TM140420HS026 | TM140420SV026.ZSO | TM140420SV026.GSO | TICKLER REFINER BYPASS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS204 |  | TM140420HS026 | TM140420EV026 | TM140420EV026 | TICKLER REFINER BYPASS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420HS027 | TM140420SV027 | TM140420SV027 | DILUTION WATER TO TICKLER REFINER FEED ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS204 |  | TM140420HS027 | TM140420SV027.ZSC | TM140420SV027.GSC | DILUTION WATER TO TICKLER REFINER FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS204 |  | TM140420HS027 | TM140420SV027.ZSO | TM140420SV027.GSO | DILUTION WATER TO TICKLER REFINER FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS204 |  | TM140420HS027 | TM140420EV027 | TM140420EV027 | DILUTION WATER TO TICKLER REFINER FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420HS028 | TM140420SV028 | TM140420SV028 | SEALING WATER TO TICKLER REFINER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS204 |  | TM140420HS028 | TM140420SV028.ZSC | TM140420SV028.GSC | SEALING WATER TO TICKLER REFINER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS204 |  | TM140420HS028 | TM140420SV028.ZSO | TM140420SV028.GSO | SEALING WATER TO TICKLER REFINER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS204 |  | TM140420HS028 | TM140420EV028 | TM140420EV028 | SEALING WATER TO TICKLER REFINER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD202 |  | TM140420FS029 | TM140420FS029 | TM140420FS029.L | SEALING WATER TO TICKLER REFINER FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420TIZ030 | TM140420TE030 |  | TICKLER REFINER OUTLET TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | B | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA201 |  | TM140420TIZ030 | TM140420TT030 | TM140420TT030.MV | TICKLER REFINER OUTLET TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD202 |  | TM140420TIZ030 | TM140420TS030 | TM140420TS030.H | TICKLER REFINER OUTLET TEMPERATURE HIGH | TS | Temperature switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 150 | ˚C | [7 empty] | Temp. High | Not Temp. High | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD202 |  | TM140420GS031 | TM140420GS031.A | TM140420GS031.A.START | TICKLER REFINER FILLINGS POSITION START | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Start | Start | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD202 |  | TM140420GS031 | TM140420GS031.B | TM140420GS031.B.OPEN | TICKLER REFINER FILLINGS POSITION OPEN | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD202 |  | TM140420GS031 | TM140420GS031.C | TM140420GS031.C.SAF | TICKLER REFINER FILLINGS POSITION SAFETY | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Safety | Safety | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 | MCC |  | TM140420EC033 | TM140420ET033 | TM140420ET033.MV | TICKLER REFINER POWER | ET | Power transmitter | MCC | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | MCC | 0 | 355 | kW | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420CB01 |  | TM140420EC033 | TM140420EI033 | TM140420EI033.IND | TICKLER REFINER POWER | EI | Local digital indicator | Field | DCS | AO | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 100 | % | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420FC034 | TM140420FE034 |  | TICKLER REFINER TO MACHINE CHEST FLOW | FE | Magnetic flow Sensor | Field
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 |  | TM140420FC034 | TM140420FT034 | TM140420FT034.MV | TICKLER REFINER TO MACHINE CHEST FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 3600 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 | TM1404ASD111 | TM140420FC034 | TM140420FV034 | TM140420FV034.OUT | TICKLER REFINER TO MACHINE CHEST FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420FC035 | TM140420FE035 |  | TICKLER REFINER RECIRCULATION FLOW | FE | Magnetic flow Sensor | Field
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 |  | TM140420FC035 | TM140420FT035 | TM140420FT035.MV | TICKLER REFINER RECIRCULATION FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1800 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 | TM1404ASD111 | TM140420FC035 | TM140420FV035 | TM140420FV035.OUT | TICKLER REFINER RECIRCULATION FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420WC036 | TM140420WX036 | TM140420WX036.SOF | TICKLER REFINER PRODUCTION | WX | DCS software function | DCS | DCS |  | Software function
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420AI037 | TM140420AE037 |  | TICKLER REFINER FREENESS | AE | Freeness sensor | Field
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 |  | TM140420AI037 | TM140420AT037 | TM140420AT037.MV | TICKLER REFINER FREENESS | AT | Freeness transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 15 | 750 | ml CSF | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD111 |  | TM140420AI037 | TM140420AS037 | TM140420AS037.MV | TICKLER REFINER FREENESS | AS | Freeness transmitter Stop Sampling | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420XS038 | TM140420CB01 | TM110011CB01 | TICKLER REFINER CONTROL | CB | Local Control Box | Field |  |  |  | 230 VAC | [24 empty] | 4
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420CB01 |  | TM140420XS038 | TM140420H11 038 | TM140420H11 038.RUN/F | TICKLER REFINER MOTOR RUN / FAULT | H1 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Run | Run | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420CB01 |  | TM140420XS038 | TM140420H21 038 | TM140420H21 038.L/F | TICKLER REFINER LOAD / FAULT | H2 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Load | Load | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420CB01 |  | TM140420XS038 | TM140420H22 038 | TM140420H22 038.REL/F | TICKLER REFINER RELEASE / FAULT | H2 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Release | Release | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420CB01 |  | TM140420XS038 | TM140420H23 038 | TM140420H23 038.FAULT | TICKLER REFINER FAULT | H2 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Fault | Fault | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420CB01 |  | TM140420XS038 | TM140420S10 038 | TM140420S10 038.ESTOP | TICKLER REFINER PANEL E - STOP | S1 | E - Stop Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | E - Stop | Not E - Stop | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420CB01 |  | TM140420XS038 | TM140420S11 038 | TM140420S11 038.START | TICKLER REFINER START | S1 | Illuminated Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Start | Start | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420CB01 |  | TM140420XS038 | TM140420S12 038 | TM140420S12 038.STOP | TICKLER REFINER STOP | S1 | Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Stop | Not Stop | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420CB01 |  | TM140420XS038 | TM140420S20 038 | TM140420S20 038.L/D | OPERATING MODE SELECT SWITCH - LOCAL/DCS | S2 | Select Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | DCS | Local | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420CB01 |  | TM140420XS038 | TM140420S21 038 | TM140420S21 038.LOAD | TICKLER REFINER LOAD | S2 | Illuminated Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Load | Load | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420CB01 |  | TM140420XS038 | TM140420S22 038 | TM140420S22 038.RELEASE | TICKLER REFINER RELEASE | S2 | Illuminated Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Release | Release | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420CB01 |  | TM140420XS038 | TM140420S23 038 | TM140420S23 038.FAST | TICKLER REFINER FAST | S2 | Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Fast | Fast | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420CB01 |  | TM140420XS038 | TM140420S24 038 | TM140420S24 038.TEST | TICKLER REFINER CB LAMP TEST | S2 | Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Lamp Test | Lamp Test | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420EC039 | TM140420EX039 | TM140420EX039.SOF | TICKLER REFINER POWER | EX | DCS software function | DCS | DCS |  | Software function | [25 empty] | B
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 |  | TM140420PC045 | TM140420PT045 | TM140420PT045.MV | SWEETENER PUMP OUTLET OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 |  | TM140420LC051 | TM140420LT051 | TM140420LT051.MV | MACHINE CHEST LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 5000 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420HS052 | TM140420SV052 | TM140420SV052 | MACHINE CHEST DISCHAGE ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS112 |  | TM140420HS052 | TM140420SV052.ZSC | TM140420SV052.GSC | MACHINE CHEST DISCHAGE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS112 |  | TM140420HS052 | TM140420SV052.ZSO | TM140420SV052.GSO | MACHINE CHEST DISCHAGE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS112 |  | TM140420HS052 | TM140420EV052 | TM140420EV052 | MACHINE CHEST DISCHAGE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420NC053 | TM140420NE053 |  | MACHINE CHEST PUMP OUTLET CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230 VAC
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 |  | TM140420NC053 | TM140420NT053 | TM140420NT053.MV | MACHINE CHEST PUMP OUTLET CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 6 | %C | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD111 |  | TM140420NC053 | TM140420NS053 | TM140420NS053.MV | MACHINE CHEST PUMP OUTLET CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 | TM1404ASD111 | TM140420NC053 | TM140420NV053 | TM140420NV053.OUT | MACHINE CHEST PUMP OUTLET CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA111 |  | TM140420PC054 | TM140420PT054 | TM140420PT054.MV | MACHINE CHEST PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420FC055 | TM140420FE055 |  | MACHINE CHEST PUMP OUTLET FLOW | FE | Magnetic flow Sensor | Field
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA102 |  | TM140420FC055 | TM140420FT055 | TM140420FT055.MV | MACHINE CHEST PUMP OUTLET FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 3600 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420FC055 | TM140420FV055 | TM140420FV055.OUT | MACHINE CHEST PUMP OUTLET FLOW CV SETPOINT | FV | Basic Weight Valve | [29 empty] | C
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA102 |  | TM140420FC055 | TM140420FY055 | TM140420FY055.MV | MACHINE CHEST PUMP OUTLET FLOW CV POSITION FEEDBACK | FY | Valve Position Feedback | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD101 |  | TM140420FC055 | TM140420FV055.ZSC | TM140420FV055.GSC | MACHINE CHEST PUMP OUTLET FLOW CV CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD101 |  | TM140420FC055 | TM140420FV055.ZSO | TM140420FV055.GSO | MACHINE CHEST PUMP OUTLET FLOW CV OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD101 |  | TM140420FC055 | TM140420FV055.STP | TM140420FV055.STP | MACHINE CHEST PUMP OUTLET FLOW CV CLOSE COMMAND | STP | Close Command | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [11 empty] | Close | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD101 |  | TM140420FC055 | TM140420FV055.STO | TM140420FV055.STO | MACHINE CHEST PUMP OUTLET FLOW CV OPEN COMMAND | STO | Open Command | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [11 empty] | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD111 |  | TM140420FS057 | TM140420FS057 | TM140420FS057.L | SEALING WATER TO MACHINE CHEST PUMP 1 FLOW | FS | Flow Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA202 |  | TM140420LI061 | TM140420LT061 | TM140420LT061.MV | SILO LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3000 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420HS062 | TM140420SV062 | TM140420SV062 | WHITE WATER TO SILO ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS205 |  | TM140420HS062 | TM140420SV062.ZSC | TM140420SV062.GSC | WHITE WATER TO SILO ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS205 |  | TM140420HS062 | TM140420SV062.ZSO | TM140420SV062.GSO | WHITE WATER TO SILO ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS205 |  | TM140420HS062 | TM140420EV062 | TM140420EV062 | WHITE WATER TO SILO ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140435TC020 | TM140435TE020 |  | SILO TEMPERATURE | TE | Temperature Sensor | Field
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA202 |  | TM140435TC020 | TM140435TT020 | TM140435TT020.MV | SILO TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA202 | TM1404ASD201 | TM140435TC020 | TM140435TV020 | TM140435TV020.OUT | SILO TEMPERATURE CV SETPOINT | TV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420AI064 | TM140420AE064 |  | SILO CHANNEL OVERFLOW PARTICLE CHARGE DETECT | AE | PCD sensor | Field | DCS
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA202 |  | TM140420AI064 | TM140420AT064 | TM140420AT064.MV | SILO CHANNEL OVERFLOW PARTICLE CHARGE DETECT | AT | PCD transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | -150 | -30 | µEQ/l | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD202 |  | TM140420AI064 | TM140420AS064 | TM140420AS064.INT | SILO CHANNEL OVERFLOW PARTICLE CHARGE INTERLOCK | AS | PCD transmitter Stop Sampling | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420AC065 | TM140420AE065 |  | SILO PH | AE | pH Sensor | Field | DCS
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA202 |  | TM140420AC065 | TM140420AT065 | TM140420AT065.MV | SILO PH | AT | pH Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 14 | Ph | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420HS066 | TM140420SV066 | TM140420SV066 | MACHINE CHEST PUMP OUTLET TO SILO ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 0
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS102 |  | TM140420HS066 | TM140420SV066.ZSC | TM140420SV066.GSC | MACHINE CHEST PUMP OUTLET TO SILO ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS102 |  | TM140420HS066 | TM140420SV066.ZSO | TM140420SV066.GSO | MACHINE CHEST PUMP OUTLET TO SILO ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS102 |  | TM140420HS066 | TM140420EV066 | TM140420EV066 | MACHINE CHEST PUMP OUTLET TO SILO ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420HS067 | TM140420SV067 | TM140420SV067 | MACHINE CHEST PUMP OUTLET TO RECOVERED STOCK CHEST ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 0
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS102 |  | TM140420HS067 | TM140420SV067.ZSC | TM140420SV067.GSC | MACHINE CHEST PUMP OUTLET TO RECOVERED STOCK CHEST ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS102 |  | TM140420HS067 | TM140420SV067.ZSO | TM140420SV067.GSO | MACHINE CHEST PUMP OUTLET TO RECOVERED STOCK CHEST ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS102 |  | TM140420HS067 | TM140420EV067 | TM140420EV067 | MACHINE CHEST PUMP OUTLET TO RECOVERED STOCK CHEST ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420HS072 | TM140420SV072 | TM140420SV072 | SEALING WATER TO FAN PUMP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS101 |  | TM140420HS072 | TM140420SV072.ZSC | TM140420SV072.GSC | SEALING WATER TO FAN PUMP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS101 |  | TM140420HS072 | TM140420SV072.ZSO | TM140420SV072.GSO | SEALING WATER TO FAN PUMP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS101 |  | TM140420HS072 | TM140420EV072 | TM140420EV072 | SEALING WATER TO FAN PUMP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD101 |  | TM140420FS073 | TM140420FS073 | TM140420FS073.L | SEALING WATER TO FAN PUMP FLOW L A | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420HS075 | TM140420SV075 | TM140420SV075 | FAN PUMP OUTLET ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS101 |  | TM140420HS075 | TM140420SV075.ZSC | TM140420SV075.GSC | FAN PUMP OUTLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS101 |  | TM140420HS075 | TM140420SV075.ZSO | TM140420SV075.GSO | FAN PUMP OUTLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS101 |  | TM140420HS075 | TM140420EV075 | TM140420EV075 | FAN PUMP OUTLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA102 | TM1404ASD102 | TM140420HC078 | TM140420HV078 | TM140420HV078.OUT | 1ST STAGE APPROACH SCREEN REJECT CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420XI079 | TM140420XE079 |  | 1ST STAGE APPROACH SCREEN MOTOR VIBRATION 1 | XE | Vibration sensor | Field | [28 empty] | C | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA102 |  | TM140420XI079 | TM140420XT079 | TM140420XT079.MV | 1ST STAGE APPROACH SCREEN MOTOR VIBRATION 1 | XT | Vibration transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | [22 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA102 |  | TM140420PI081 | TM140420PT081 | TM140420PT081.MV | 1ST STAGE APPROACH SCREEN FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA102 |  | TM140420PI082 | TM140420PT082 | TM140420PT082.MV | 1ST STAGE APPROACH SCREEN ACCEPT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420PDI083 | TM140420PDX083 | TM140420PDX083.SOF | 1ST STAGE APPROACH SCREEN DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420FI084 | TM140420FE084 |  | 1ST STAGE APPROACH SCREEN REJECT FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | B
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA102 |  | TM140420FI084 | TM140420FT084 | TM140420FT084.MV | 1ST STAGE APPROACH SCREEN REJECT FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 2000 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420HS085 | TM140420SV085 | TM140420SV085 | FROM 1ST STAGE APPROACH SCREENTO SILO CHANNEL ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS101 |  | TM140420HS085 | TM140420SV085.ZSC | TM140420SV085.GSC | FROM 1ST STAGE APPROACH SCREENTO SILO CHANNEL ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS101 |  | TM140420HS085 | TM140420SV085.ZSO | TM140420SV085.GSO | FROM 1ST STAGE APPROACH SCREENTO SILO CHANNEL ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS101 |  | TM140420HS085 | TM140420EV085 | TM140420EV085 | FROM 1ST STAGE APPROACH SCREENTO SILO CHANNEL ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420HS086 | TM140420SV086 | TM140420SV086 | SEALING WATER TO 1ST STAGE APPROACH SCREEN ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS101 |  | TM140420HS086 | TM140420SV086.ZSC | TM140420SV086.GSC | SEALING WATER TO 1ST STAGE APPROACH SCREEN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS101 |  | TM140420HS086 | TM140420SV086.ZSO | TM140420SV086.GSO | SEALING WATER TO 1ST STAGE APPROACH SCREEN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS101 |  | TM140420HS086 | TM140420EV086 | TM140420EV086 | SEALING WATER TO 1ST STAGE APPROACH SCREEN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD101 |  | TM140420FS087 | TM140420FS087 | TM140420FS087.L | SEALING WATER TO 1ST STAGE APPROACH SCREEN FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA201 |  | TM140420PI091 | TM140420PT091 | TM140420PT091.MV | 2ND STAGE APPROACH SCREEN FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA201 |  | TM140420PI092 | TM140420PT092 | TM140420PT092.MV | 2ND STAGE APPROACH SCREEN ACCEPT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420PDI093 | TM140420PDX093 | TM140420PDX093.SOF | 2ND STAGE APPROACH SCREEN DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420KC094 | TM140420SV094 | TM140420SV094 | 2ND STAGE APPROACH SCREEN REJECT ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD202 |  | TM140420KC094 | TM140420SV094.ZSC | TM140420SV094.GSC | 2ND STAGE APPROACH SCREEN REJECT ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD202 |  | TM140420KC094 | TM140420SV094.ZSO | TM140420SV094.GSO | 2ND STAGE APPROACH SCREEN REJECT ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD202 | TM1404ASD201 | TM140420KC094 | TM140420EV094 | TM140420EV094 | 2ND STAGE APPROACH SCREEN REJECT ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA201 | TM1404ASD201 | TM140420HC095 | TM140420HV095 | TM140420HV095.OUT | FROM 2ND STAGE APPROACH SCREEN TO SILO CHANNEL CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420HS096 | TM140420SV096 | TM140420SV096 | SEALING WATER TO 2ND STAGE APPROACH SCREEN ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS203 |  | TM140420HS096 | TM140420SV096.ZSC | TM140420SV096.GSC | SEALING WATER TO 2ND STAGE APPROACH SCREEN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS203 |  | TM140420HS096 | TM140420SV096.ZSO | TM140420SV096.GSO | SEALING WATER TO 2ND STAGE APPROACH SCREEN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBS203 |  | TM140420HS096 | TM140420EV096 | TM140420EV096 | SEALING WATER TO 2ND STAGE APPROACH SCREEN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBD202 |  | TM140420FS097 | TM140420FS097 | TM140420FS097.L | SEALING WATER TO 2ND STAGE APPROACH SCREEN FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA102 |  | TM140420LC101 | TM140420LT101 | TM140420LT101.MV | WIRE WHITE WATER TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3300 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA102 | TM1404ASD102 | TM140420HC103 | TM140420HV103 | TM140420HV103.OUT | W.W OVERFLOW CHEST PUMP TO SILO CHANNEL CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA102 | TM1404ASD102 | TM140420HC104 | TM140420HV104 | TM140420HV104.OUT | W.W OVERFLOW CHEST PUMP TO W.W COLLECTION TANK CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420XI106 | TM140420XE106 |  | 1ST STAGE APPROACH SCREEN MOTOR VIBRATION 2 | XE | Vibration sensor | Field | [28 empty] | C | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA102 |  | TM140420XI106 | TM140420XT106 | TM140420XT106.MV | 1ST STAGE APPROACH SCREEN MOTOR VIBRATION 2 | XT | Vibration transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | [22 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA202 |  | TM140420PC111 | TM140420PT111 | TM140420PT111.MV | HEADBOX PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA102 | TM1404ASD102 | TM140420HC112 | TM140420HV112 | TM140420HV112.OUT | HEADBOX RECIRCULATION CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140420 |  |  | TM140420FI114 | TM140420FE114 |  | HEADBOX RECIRCULATION FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | B
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM1404JBA102 |  | TM140420FI114 | TM140420FT114 | TM140420FT114.MV | HEADBOX RECIRCULATION FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 5000 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140415 |  |  | TM140415FC005 | TM140415FE005 |  | WET STRENGHT AGENT TO MIXING CHEST PUMP FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-4051 | TM140415 | TM1404JBA111 |  | TM140415FC005 | TM140415FT005 | TM140415FT005.MV | WET STRENGHT AGENT TO MIXING CHEST PUMP FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | hold | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140415 |  |  | TM140415FC006 | TM140415FE006 |  | DRY STRENGHT AGENT TO MACHINE CHEST PUMP FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-4051 | TM140415 | TM1404JBA111 |  | TM140415FC006 | TM140415FT006 | TM140415FT006.MV | DRY STRENGHT AGENT TO MACHINE CHEST PUMP FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | hold | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140415 |  |  | TM140415FC007 | TM140415FE007 |  | SOFT AGENT TO MIXING CHEST PUMP FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-4051 | TM140415 | TM1404JBA111 |  | TM140415FC007 | TM140415FT007 | TM140415FT007.MV | SOFT AGENT TO MIXING CHEST PUMP FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | hold | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140415 |  |  | TM140415FC008 | TM140415FE008 |  | CMC TO FAN PUMP FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-4051 | TM140415 | TM1404JBA102 |  | TM140415FC008 | TM140415FT008 | TM140415FT008.MV | CMC TO FAN PUMP FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | hold | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140415 |  |  | TM140415HS069 | TM140415SV069 | TM140415SV069 | WET STRENGHT AGENT TO MIXING CHEST PUMP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4051 | TM140415 | TM1404JBS111 |  | TM140415HS069 | TM140415SV069.ZSC | TM140415SV069.GSC | WET STRENGHT AGENT TO MIXING CHEST PUMP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140415 | TM1404JBS111 |  | TM140415HS069 | TM140415SV069.ZSO | TM140415SV069.GSO | WET STRENGHT AGENT TO MIXING CHEST PUMP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140415 | TM1404JBS111 |  | TM140415HS069 | TM140415EV069 | TM140415EV069 | WET STRENGHT AGENT TO MIXING CHEST PUMP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140415 |  |  | TM140415HS070 | TM140415SV070 | TM140415SV070 | DRY STRENGHT AGENT TO MACHINE CHEST PUMP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4051 | TM140415 | TM1404JBS112 |  | TM140415HS070 | TM140415SV070.ZSC | TM140415SV070.GSC | DRY STRENGHT AGENT TO MACHINE CHEST PUMP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140415 | TM1404JBS112 |  | TM140415HS070 | TM140415SV070.ZSO | TM140415SV070.GSO | DRY STRENGHT AGENT TO MACHINE CHEST PUMP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140415 | TM1404JBS112 |  | TM140415HS070 | TM140415EV070 | TM140415EV070 | DRY STRENGHT AGENT TO MACHINE CHEST PUMP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140415 |  |  | TM140415HS071 | TM140415SV071 | TM140415SV071 | SOFT AGENT TO MIXING CHEST PUMP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4051 | TM140415 | TM1404JBS111 |  | TM140415HS071 | TM140415SV071.ZSC | TM140415SV071.GSC | SOFT AGENT TO MIXING CHEST PUMP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140415 | TM1404JBS111 |  | TM140415HS071 | TM140415SV071.ZSO | TM140415SV071.GSO | SOFT AGENT TO MIXING CHEST PUMP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140415 | TM1404JBS111 |  | TM140415HS071 | TM140415EV071 | TM140415EV071 | SOFT AGENT TO MIXING CHEST PUMP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140415 |  |  | TM140415HS072 | TM140415SV072 | TM140415SV072 | CMC TO FAN PUMP ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4051 | TM140415 | TM1404JBS101 |  | TM140415HS072 | TM140415SV072.ZSC | TM140415SV072.GSC | CMC TO FAN PUMP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140415 | TM1404JBS101 |  | TM140415HS072 | TM140415SV072.ZSO | TM140415SV072.GSO | CMC TO FAN PUMP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4051 | TM140415 | TM1404JBS101 |  | TM140415HS072 | TM140415EV072 | TM140415EV072 | CMC TO FAN PUMP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
WHITE WATER AND FIBRE RECOVERY
P-OKITM07-10-320-07-PID-4055 | TM140421 |  |  | TM140421FC001 | TM140421FE001 |  | W.W TO DISC FILTER FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA112 |  | TM140421FC001 | TM140421FT001 | TM140421FT001.MV | W.W TO DISC FILTER FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 5000 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA112 | TM1404ASD112 | TM140421FC001 | TM140421FV001 | TM140421FV001.OUT | W.W TO DISC FILTER FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA101 |  | TM140421LC002 | TM140421LT002 | TM140421LT002.MV | SUPER CLARIFIED TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA101 | TM1404ASD101 | TM140421LC002 | TM140421LV002 | TM140421LV002.OUT | SUPER CLARIFIED TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 |  |  | TM140421FFC003 | TM140421FE003 |  | SWEETENER STOCK FLOW | FE | Magnetic flow Sensor | Field
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA112 |  | TM140421FFC003 | TM140421FT003 | TM140421FT003.MV | SWEETENER STOCK FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1800 | l / min | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA112 | TM1404ASD112 | TM140421FFC003 | TM140421FV003 | TM140421FV003.OUT | SWEETENER STOCK FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA101 |  | TM140421LC004 | TM140421LT004 | TM140421LT004.MV | CLARIFIED TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA101 | TM1404ASD101 | TM140421LC004 | TM140421LV004 | TM140421LV004.OUT | CLARIFIED TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA101 |  | TM140421LC005 | TM140421LT005 | TM140421LT005.MV | CLOUDY FILTRATE TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3300 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA101 | TM1404ASD101 | TM140421LC005 | TM140421LV005 | TM140421LV005.OUT | CLOUDY FILTRATE TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA101 |  | TM140421LC006 | TM140421LT006 | TM140421LT006.MV | RECOVERED STOCK CHEST LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA112 |  | TM140421LC007 | TM140421LT007 | TM140421LT007.MV | W.W. COLLECTION TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10000 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA112 | TM1404ASD112 | TM140421LC007 | TM140421LV007A | TM140421LV007A.OUT | W.W. COLLECTION TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA112 | TM1404ASD112 | TM140421LC007 | TM140421LV007B | TM140421LV007B.PRO | W.W. COLLECTION TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA101 |  | TM140421PI008 | TM140421PT008 | TM140421PT008.MV | CWW LP SHOWER FILTER INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 |  |  | TM140421PDI009 | TM140421PDX009 | TM140421PDX009.SOF | CWW LP SHOWER FILTER DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function |  |  |  | 0 | 2 | Bar.g | [19 empty] | B
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA101 |  | TM140421PC010 | TM140421PT010 | TM140421PT010.MV | CWW LP SHOWER FILTER FILTER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 |  |  | TM140421HS011 | TM140421SV011 | TM140421SV011 | W.W TO DISC FILTER SHOWERS ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBS201 |  | TM140421HS011 | TM140421SV011.ZSC | TM140421SV011.GSC | W.W TO DISC FILTER SHOWERS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBS201 |  | TM140421HS011 | TM140421SV011.ZSO | TM140421SV011.GSO | W.W TO DISC FILTER SHOWERS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBS201 |  | TM140421HS011 | TM140421EV011 | TM140421EV011 | W.W TO DISC FILTER SHOWERS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | MCC |  | TM140421EI012 | TM140421ET012 | TM140421ET012.MV | DISC FILTER TORQUE | ET | Power transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA201 |  | TM140421PI013 | TM140421PT013 | TM140421PT013.MV | DISC FILTER VACUUM | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBD201 |  | TM140421SS014 | TM140421GS014A | TM140421GS014A.SEC | DISC FILTER SECTOR COUNTER SECTOR PULSE | GS | Proximity Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Sector Pulse | Sector Pulse | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBD201 |  | TM140421SS014 | TM140421GS014B | TM140421GS014B.ROT | DISC FILTER SECTOR COUNTER ROTATION PULSE | GS | Proximity Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Rotation Pulse | Rotation Pulse | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBD201 |  | TM140421SS015 | TM140421SS015 | TM140421SS015.L | DISC FILTER SPEED REPULPER SPEED LOW | SS | Speed Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Speed Low | Not Speed Low | [10 empty] | 1 | Andritz
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBD201 |  | TM140421XS016 | TM140421S9 016 | TM140421S9 016.DCS/LOCAL | DISC FILTER LOCAL OPERATION MAINDRIVE DCS/LOCAL | S9 | Selector Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Jog | Jog | [10 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBD201 |  | TM140421XS016 | TM140421S11 016 | TM140421S11 016.JOG | DISC FILTER LOCAL OPERATION MAINDRIVE JOG FORWARD | S11 | Push button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Local | DCS | [10 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBD201 |  | TM140421XS017 | TM140421S9 017 | TM140421S9 017.JOG | DISC FILTER LOCAL OPERATION SHOWER OSCILLATION DCS/LOCAL | S9 | Selector Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Jog | Jog | [10 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBD201 |  | TM140421XS017 | TM140421S11 017 | TM140421S11 017.DCS/LOCAL | DISC FILTER LOCAL OPERATION SHOWER OSCILLATION LOCAL START | S11 | Push button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Local | DCS | [10 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA101 |  | TM140421PI018 | TM140421PT018 | TM140421PT018.MV | SCWW SHOWER FILTER INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 7 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 |  |  | TM140421PDI019 | TM140421PDX019 | TM140421PDX019.SOF | SCWW SHOWER FILTER DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function |  |  |  | 0 | 2 | Bar.g | [19 empty] | B
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA101 |  | TM140421PC020 | TM140421PT020 | TM140421PT020.MV | SCWW SHOWER FILTER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 7 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA201 |  | TM140421LC021 | TM140421LT021 | TM140421LT021.MV | DISC FILTER LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 2000 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA112 |  | TM140421PC022 | TM140421PT022 | TM140421PT022.MV | TM AREA CRC PUMP OUTLET WHITE WATER PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 7 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA101 |  | TM140421PI024 | TM140421PT024 | TM140421PT024.MV | CWW HP SHOWER FILTER FILTER INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 25 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 |  |  | TM140421PDI025 | TM140421PDX025 | TM140421PDX025.SOF | CWW HP SHOWER FILTER DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function |  |  |  | 0 | 2 | Bar.g | [19 empty] | B
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA101 |  | TM140421PC026 | TM140421PT026 | TM140421PT026.MV | CWW HP SHOWER FILTER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 25 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBD201 |  | TM140421XS028 | TM140421S10 028 | TM140421S10 028.ESTOP | DISC FILTER LOCAL OPERATION MAINDRIVE E-STOP | S10 | E - Stop Push Button | +CP01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | E-Stop | [11 empty] | 4 | Andritz
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421CP01 |  | TM140421XS031 | TM140421S1.031 | TM140421S1.031 | CWW LP SHOWER FILTER LOCAL PANEL | S1 | Differential Pressure High alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421CP01 |  | TM140421XS031 | TM140421S2.031 | TM140421S2.031 | CWW LP SHOWER FILTER LOCAL PANEL | S2 | Flush alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421CP01 |  | TM140421XS031 | TM140421S3.031 | TM140421S3.031 | CWW LP SHOWER FILTER LOCAL PANEL | S3 | Power Failure alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421CP02 |  | TM140421XS032 | TM140421S1.032 | TM140421S1.032 | CWW HP SHOWER FILTER LOCAL PANEL | S1 | Differential Pressure High alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421CP02 |  | TM140421XS032 | TM140421S2.032 | TM140421S2.032 | CWW HP SHOWER FILTER LOCAL PANEL | S2 | Flush alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421CP02 |  | TM140421XS032 | TM140421S3.032 | TM140421S3.032 | CWW HP SHOWER FILTER LOCAL PANEL | S3 | Power Failure alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421CP03 |  | TM140421XS033 | TM140421S1.033 | TM140421S1.033 | SCWW SHOWER FILTER LOCAL PANEL | S1 | Differential Pressure High alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421CP03 |  | TM140421XS033 | TM140421S2.033 | TM140421S2.033 | SCWW SHOWER FILTER LOCAL PANEL | S2 | Flush alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421CP03 |  | TM140421XS033 | TM140421S3.033 | TM140421S3.033 | SCWW SHOWER FILTER LOCAL PANEL | S3 | Power Failure alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 4
P-OKITM07-10-320-07-PID-4055 | TM140421 |  |  | TM140421HS036 | TM140421SV036 | TM140421SV036 | W.W TO DISC FILTER SHOWERS ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBS201 |  | TM140421HS036 | TM140421SV036.ZSC | TM140421SV036.GSC | W.W TO DISC FILTER SHOWERS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBS201 |  | TM140421HS036 | TM140421SV036.ZSO | TM140421SV036.GSO | W.W TO DISC FILTER SHOWERS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBS201 |  | TM140421HS036 | TM140421EV036 | TM140421EV036 | W.W TO DISC FILTER SHOWERS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 |  |  | TM140421FC037 | TM140421FE037 |  | W.W TO DISC FILTER REPULPER FLOW | FE | Magnetic Flow Sensor | Field | DCS
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA201 |  | TM140421FC037 | TM140421FT037 | TM140421FT037.MV | W.W TO DISC FILTER REPULPER FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1000 | l/min | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA201 | TM1404ASD201 | TM140421FC037 | TM140421FV037 | TM140421FV037.OUT | W.W TO DISC FILTER REPULPER FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA201 |  | TM140421PC038 | TM140421PT038 | TM140421PT038.MV | DISC FILTER SHOWERS PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA101 | TM1404ASD101 | TM140421HC039 | TM140421HV039 | TM140421HV039.OUT | FRESH WATER TO CLOUDY FILTRATE TANK CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBD101 |  | TM140421FS040 | TM140421FS040 | TM140421FS040.L | SEALING WATER TO REC PULP CHEST PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA201 |  | TM140421PI041 | TM140421PT041 | TM140421PT041.MV | W.W TO DISC FILTER SHOWERS PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 |  |  | TM140421HS045 | TM140421SV045 | TM140421SV045 | REC PULP CHEST PUMP OUTLET TO BROKE INTERIM TOWER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBS111 |  | TM140421HS045 | TM140421SV045.ZSC | TM140421SV045.GSC | REC PULP CHEST PUMP OUTLET TO BROKE INTERIM TOWER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBS111 |  | TM140421HS045 | TM140421SV045.ZSO | TM140421SV045.GSO | REC PULP CHEST PUMP OUTLET TO BROKE INTERIM TOWER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBS111 |  | TM140421HS045 | TM140421EV045 | TM140421EV045 | REC PULP CHEST PUMP OUTLET TO BROKE INTERIM TOWER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 |  |  | TM140421HS046 | TM140421SV046 | TM140421SV046 | REC PULP CHEST PUMP OUTLET TO TM 14.1 MIXING CHEST ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBS111 |  | TM140421HS046 | TM140421SV046.ZSC | TM140421SV046.GSC | REC PULP CHEST PUMP OUTLET TO TM 14.1 MIXING CHEST ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBS111 |  | TM140421HS046 | TM140421SV046.ZSO | TM140421SV046.GSO | REC PULP CHEST PUMP OUTLET TO TM 14.1 MIXING CHEST ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBS111 |  | TM140421HS046 | TM140421EV046 | TM140421EV046 | REC PULP CHEST PUMP OUTLET TO TM 14.1 MIXING CHEST ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA101 |  | TM140421PC050 | TM140421PT050 | TM140421PT050.MV | CLOUDY CIRCULATION PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA112 |  | TM140421PC136 | TM140421PT136 | TM140421PT136.MV | YANKEE-TRIM PULPER & OVER FLOW PUMP WHITE WATER PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 |  |  | TM140421HS137 | TM140421SV137 | TM140421SV137 | PULP FROM RECOVERED STOCK CHEST ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBS101 |  | TM140421HS137 | TM140421SV137.ZSC | TM140421SV137.GSC | PULP FROM RECOVERED STOCK CHEST ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBS101 |  | TM140421HS137 | TM140421SV137.ZSO | TM140421SV137.GSO | PULP FROM RECOVERED STOCK CHEST ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBS101 |  | TM140421HS137 | TM140421EV137 | TM140421EV137 | PULP FROM RECOVERED STOCK CHEST ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 |  |  | TM140421NC138 | TM140421NE138 |  | REC PULP CHEST PUMP OUTLET CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230 VAC | [24 empty] | B
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA101 |  | TM140421NC138 | TM140421NT138 | TM140421NT138.MV | REC PULP CHEST PUMP OUTLET CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 6 | %C | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBD101 |  | TM140421NC138 | TM140421NS138 | TM140421NS138.MV | REC PULP CHEST PUMP OUTLET CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA101 | TM1404ASD101 | TM140421NC138 | TM140421NV138 | TM140421NV138.OUT | REC PULP CHEST PUMP OUTLET CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA101 |  | TM140421PC140 | TM140421PT140 | TM140421PT140.MV | PMP DEMAND & CLEANING PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA101 |  | TM140421PC141 | TM140421PT141 | TM140421PT141.MV | SCWW HP SHOWER PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 40 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA111 |  | TM140421FI144 | TM140421FT144 | TM140421FT144.MV | WASTE WATER FROM TM14.4 FLOW | FT | Open channel flow transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 250 | m3/hr | [19 empty] | 4
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM1404JBA101 |  | TM140421PC146 | TM140421PT146 | TM140421PT146.MV | DUST SCWW PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 40 | Bar.g | [19 empty] | 4
VACUUM SYSTEM
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423LC014 | TM140423LT014 | TM110123LT014.MV | VACUUM WW TANK LEVEL | LT | DP Level Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 2500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 | TM1404ASD103 | TM140423LC014 | TM140423LV014 | TM140423LV014.OUT | VACUUM WW TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 | TM1404ASD103 | TM140423HC015 | TM140423HV015 | TM140423HV015.OUT | COOLING TOWER OUTLET BYPASS CV SETPOINT | HV | Control Valve | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBD102 |  | TM140423PS021 | TM140423PS021 | TM140423PS021.L | VACUUM PUMP 1 GEAR REDUCER LUBRICATION OIL PRESSURE | PS | Pressure switch | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBD102 |  | TM140423PS022 | TM140423PS022 | TM140423PS022.L | VACUUM PUMP 2 GEAR REDUCER LUBRICATION OIL PRESSURE | PS | Pressure switch | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423FI065 | TM140423FE065 |  | MAKE-UP WATER VACUUM SYSTEM FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423FI065 | TM140423FT065 | TM140423FT065.MV | MAKE-UP WATER VACUUM SYSTEM FLOW | FT | Magnetic flow transmitter | Field | DCS |  | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 720 | l / min | [19 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423TI066 | TM140423TE066 |  | COOLED SEAL WATER TEMPERATURE | TE | Temperature sensor | Field | [28 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423TI066 | TM140423TT066 | TM140423TT066.MV | COOLED SEAL WATER TEMPERATURE | TT | Temperature transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [19 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423PC067 | TM140423PT067 | TM140423PT067.MV | SEAL WATER TO VACUUM PUMPS PRESSURE | PT | Pressure Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 4 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 | TM1404ASD103 | TM140423PC067 | TM140423PV067 | TM140423PV067.OUT | SEAL WATER TO VACUUM PUMPS PRESSURE CV SETPOINT | PV | Control Valve | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423PI073 | TM140423PT073 | TM140423PT073.MV | VACUUM PUMP 1 PRESSURE | PT | Pressure Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423PI074 | TM140423PT074 | TM140423PT074.MV | VACUUM PUMP 1 PRESSURE | PT | Pressure Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423PI075 | TM140423PT075 | TM140423PT075.MV | VACUUM PUMP 2 PRESSURE | PT | Pressure Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423PI076 | TM140423PT076 | TM140423PT076.MV | VACUUM PUMP 2 PRESSURE | PT | Pressure Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423TI079 | TM140423TE079 |  | COOLING TOWER PUMP 2 OUTLET TEMPERATURE | TE | Temperature sensor | Field | [28 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423TI079 | TM140423TT079 | TM140423TT079.MV | COOLING TOWER PUMP 2 OUTLET TEMPERATURE | TT | Temperature transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [19 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423HS081 | TM140423SV081 | TM140423SV081 | VACUUM PUMP 1 DRAIN ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS102 |  | TM140423HS081 | TM140423SV081.ZSC | TM140423SV081.GSC | VACUUM PUMP 1 DRAIN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS102 |  | TM140423HS081 | TM140423SV081.ZSO | TM140423SV081.GSO | VACUUM PUMP 1 DRAIN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS102 |  | TM140423HS081 | TM140423EV081 | TM140423EV081 | VACUUM PUMP 1 DRAIN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423HS083 | TM140423SV083 | TM140423SV083 | VACUUM PUMP 2 DRAIN ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS102 |  | TM140423HS083 | TM140423SV083.ZSC | TM140423SV083.GSC | VACUUM PUMP 2 DRAIN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS102 |  | TM140423HS083 | TM140423SV083.ZSO | TM140423SV083.GSO | VACUUM PUMP 2 DRAIN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS102 |  | TM140423HS083 | TM140423EV083 | TM140423EV083 | VACUUM PUMP 2 DRAIN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423HS091 | TM140423SV091 | TM140423SV091 | VACUUM PUMP 1 COOLING WATER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS102 |  | TM140423HS091 | TM140423SV091.ZSC | TM140423SV091.GSC | VACUUM PUMP 1 COOLING WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS102 |  | TM140423HS091 | TM140423SV091.ZSO | TM140423SV091.GSO | VACUUM PUMP 1 COOLING WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS102 |  | TM140423HS091 | TM140423EV091 | TM140423EV091 | VACUUM PUMP 1 COOLING WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423FI092 | TM140423FE092 |  | COOLING WATER TO VACUUM PUMP 1 FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423FI092 | TM140423FT092 | TM140423FT092.MV | COOLING WATER TO VACUUM PUMP 1 FLOW | FT | Magnetic flow transmitter | Field | DCS |  | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 430 | l / min | [19 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423HS093 | TM140423SV093 | TM140423SV093 | VACUUM PUMP 2 COOLING WATER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS102 |  | TM140423HS093 | TM140423SV093.ZSC | TM140423SV093.GSC | VACUUM PUMP 2 COOLING WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS102 |  | TM140423HS093 | TM140423SV093.ZSO | TM140423SV093.GSO | VACUUM PUMP 2 COOLING WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS102 |  | TM140423HS093 | TM140423EV093 | TM140423EV093 | VACUUM PUMP 2 COOLING WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS |  | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423FI094 | TM140423FE094 |  | COOLING WATER TO VACUUM PUMP 2 FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423FI094 | TM140423FT094 | TM140423FT094.MV | COOLING WATER TO VACUUM PUMP 2 FLOW | FT | Magnetic flow transmitter | Field | DCS |  | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 420 | l / min | [19 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423LIS095 | TM140423LT095 | TM140423LT095.MV | VACUUM W.W PIT LEVEL | LT | Radar Level Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | mm |  | 10% | 15% | [16 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 | TM1404ASD103 | TM140423HC096 | TM140423HV096 | TM140423HV096.OUT | COOLING TOWER PUMP OUTLET TO COOLING TOWER CV SETPOINT | HV | Control Valve | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 | TM1404ASD103 | TM140423HC097 | TM140423HV097 | TM140423HV097.OUT | COOLING TOWER PUMP OUTLET TO WIRE WHITE WATER TANK CV SETPOINT | HV | Control Valve | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140323HS101 | TM140323SV101 | TM140323SV101 | VACUUM SHEAVE ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140323 | TM1404JBS102 |  | TM140323HS101 | TM140323SV101.ZSC | TM140323SV101.GSC | VACUUM SHEAVE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140323 | TM1404JBS102 |  | TM140323HS101 | TM140323SV101.ZSO | TM140323SV101.GSO | VACUUM SHEAVE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140323 | TM1404JBS102 |  | TM140323HS101 | TM140323EV101 | TM140323EV101 | VACUUM SHEAVE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423PI110 | TM140423PT110 | TM140423PT110.MV | VACUUM PUMP INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 3 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423HC113 | TM140423HV113 | TM140423HV113.OUT | ANTI-SURGE ELECTRIC BUTTERFLY VALVE FEEDBACK | HV | Control Valve | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423HC113 | TM140423HV113 | TM140423HV113.OUT | ANTI-SURGE ELECTRIC BUTTERFLY VALVE CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423LIC114 | TM140423LT114 | TM140423LT114.MV | VACUUM SEPARATOR LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 500 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 4
P-OKITM07-10-320-07-PID-3005 | TM140421 | TM1404JBA101 | TM1404ASD103 | TM140423LIC114 | TM140423LV114 | TM140423LV114.OUT | VACUUM SEPARATOR LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423TISA121 | TM140423TE121 |  | FRONT BEARING TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423TISA121 | TM140423TT121 | TM140423TT121.MV | FRONT BEARING TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423TISA122 | TM140423TE122 |  | REAR BEARING TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423TISA122 | TM140423TT122 | TM140423TT122.MV | REAR BEARING TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423TISA123 | TM140423TE123 |  | THRUST BEARING TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423TISA123 | TM140423TT123 | TM140423TT123.MV | THRUST BEARING TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423TISA124 | TM140423TE124 |  | TEMPERATURE OF STATOR WINDING U | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423TISA124 | TM140423TT124 | TM140423TT124.MV | TEMPERATURE OF STATOR WINDING U | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423TISA125 | TM140423TE125 |  | TEMPERATURE OF STATOR WINDING V | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423TISA125 | TM140423TT125 | TM140423TT125.MV | TEMPERATURE OF STATOR WINDING V | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423TISA126 | TM140423TE126 |  | TEMPERATURE OF STATOR WINDING W | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423TISA126 | TM140423TT126 | TM140423TT126.MV | TEMPERATURE OF STATOR WINDING W | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423XISA127 | TM140423XT127 |  | THE OUTPUT SHAFT VIBRATES IN THE X DIRECTION | XT | Vibration sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423XISA127 | TM140423XT127 | TM140423XT127.MV | THE OUTPUT SHAFT VIBRATES IN THE X DIRECTION | XT | Vibration transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | mm | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423XISA128 | TM140423XT128 |  | THE OUTPUT SHAFT VIBRATES IN THE Y DIRECTION | XT | Vibration sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423XISA128 | TM140423XT128 | TM140423XT128.MV | THE OUTPUT SHAFT VIBRATES IN THE Y DIRECTION | XT | Vibration transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | mm | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423TISA131 | TM140423TE131 |  | OIL SUPPLY OIL TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423TISA131 | TM140423TT131 | TM140423TT131.MV | OIL SUPPLY OIL TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423TISA132 | TM140423TE132 |  | TANK OIL TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423TISA132 | TM140423TT132 | TM140423TT132.MV | TANK OIL TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423PC133 | TM140423PT133 | TM140423PT133.MV | OIL SUPPLY PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 16 | Bar.g | [19 empty] | 4 | Sanfeng
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA202 |  | TM140423PC141 | TM140423PT141 | TM140423PT141.MV | UHLE BOX PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 | TM1404ASD103 | TM140123PC141 | TM140123PV141 | TM140123PV141.OUT | UHLE BOX PRESSURE CV SETPOINT | PV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA202 |  | TM140423PI142 | TM140423PT142 | TM140423PT142.MV | PICK-UP BOX PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA202 |  | TM140423PC143 | TM140423PT143 | TM140423PT143.MV | SUCTION PRESS ROLL PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | -1 | 0 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 | TM1404ASD103 | TM140423PC143 | TM140423PV143 | TM140423PV143.OUT | SUCTION PRESS ROLL PRESSURE CV SETPOINT | PV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423HS144 | TM140423SV144 | TM140423SV144 | VACUUM SHEAVE ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS205 |  | TM140423HS144 | TM140423SV144.ZSC | TM140423SV144.GSC | VACUUM SHEAVE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS205 |  | TM140423HS144 | TM140423SV144.ZSO | TM140423SV144.GSO | VACUUM SHEAVE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS205 |  | TM140423HS144 | TM140423EV144 | TM140423EV144 | VACUUM SHEAVE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423HS145 | TM140423SV145 | TM140423SV145 | VACUUM SHEAVE ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS205 |  | TM140423HS145 | TM140423SV145.ZSC | TM140423SV145.GSC | VACUUM SHEAVE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS205 |  | TM140423HS145 | TM140423SV145.ZSO | TM140423SV145.GSO | VACUUM SHEAVE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS205 |  | TM140423HS145 | TM140423EV145 | TM140423EV145 | VACUUM SHEAVE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 |  |  | TM140423HS146 | TM140423SV146 | TM140423SV146 | VACUUM SHEAVE ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS205 |  | TM140423HS146 | TM140423SV146.ZSC | TM140423SV146.GSC | VACUUM SHEAVE ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS205 |  | TM140423HS146 | TM140423SV146.ZSO | TM140423SV146.GSO | VACUUM SHEAVE ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBS205 |  | TM140423HS146 | TM140423EV146 | TM140423EV146 | VACUUM SHEAVE ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 4
P-OKITM07-10-320-07-PID-4053 | TM140423 | TM1404JBA103 |  | TM140423LC147 | TM140423LT147 | TM140423LT147.MV | VACUUM SEPARATOR LEVEL | LT | DP Level Transmitter | Field | DCS |  | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3000 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 4
| SHOWERS SYSTEM | [37 empty] | 4 | Cutes
P-OKITM07-10-320-07-PID-4054 | TM140421 |  |  | TM140421HS095 | TM140421SV095 | TM140421SV095 | WIRE CLEANING (FW2) SHOWER WATER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4054 | TM140421 | TM1404JBS205 |  | TM140421HS095 | TM140421SV095.ZSC | TM140421SV095.GSC | WIRE CLEANING (FW2) SHOWER WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4054 | TM140421 | TM1404JBS205 |  | TM140421HS095 | TM140421SV095.ZSO | TM140421SV095.GSO | WIRE CLEANING (FW2) SHOWER WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4054 | TM140421 | TM1404JBS205 |  | TM140421HS095 | TM140421EV095 | TM140421EV095 | WIRE CLEANING (FW2) SHOWER WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4054 | TM140421 |  |  | TM140421HS096 | TM140421SV096 | TM140421SV096 | SHEET SIDE FELT CLEANING(PW5) SHOWER WATER ON/OFF VALVE | SV | On/Off Valve
P-OKITM07-10-320-07-PID-4054 | TM140421 | TM1404JBS205 |  | TM140421HS096 | TM140421SV096.ZSC | TM140421SV096.GSC | SHEET SIDE FELT CLEANING(PW5) SHOWER WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4054 | TM140421 | TM1404JBS205 |  | TM140421HS096 | TM140421SV096.ZSO | TM140421SV096.GSO | SHEET SIDE FELT CLEANING(PW5) SHOWER WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4054 | TM140421 | TM1404JBS205 |  | TM140421HS096 | TM140421EV096 | TM140421EV096 | SHEET SIDE FELT CLEANING(PW5) SHOWER WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4054 | TM140421 |  |  | TM140421HS097 | TM140421SV097 | TM140421SV097 | FLOODED NIP (PW7) SHOWER WATER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 0
P-OKITM07-10-320-07-PID-4054 | TM140421 | TM1404JBS205 |  | TM140421HS097 | TM140421SV097.ZSC | TM140421SV097.GSC | FLOODED NIP (PW7) SHOWER WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4054 | TM140421 | TM1404JBS205 |  | TM140421HS097 | TM140421SV097.ZSO | TM140421SV097.GSO | FLOODED NIP (PW7) SHOWER WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4054 | TM140421 | TM1404JBS205 |  | TM140421HS097 | TM140421EV097 | TM140421EV097 | FLOODED NIP (PW7) SHOWER WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4054 | TM140421 |  |  | TM140421HS098 | TM140421SV098 | TM140421SV098 | TAIL CUTTER (PW3) SHOWER WATER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 0
P-OKITM07-10-320-07-PID-4054 | TM140421 | TM1404JBS205 |  | TM140421HS098 | TM140421SV098.ZSC | TM140421SV098.GSC | TAIL CUTTER (PW3) SHOWER WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4054 | TM140421 | TM1404JBS205 |  | TM140421HS098 | TM140421SV098.ZSO | TM140421SV098.GSO | TAIL CUTTER (PW3) SHOWER WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4054 | TM140421 | TM1404JBS205 |  | TM140421HS098 | TM140421EV098 | TM140421EV098 | TAIL CUTTER (PW3) SHOWER WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
FRESH WATER
P-OKITM07-10-320-07-PID-3709 | TM140422 | TM1404JBA102 |  | TM140422LC002 | TM140422LT002 | TM140422LT002.MV | WARM WATER TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3300 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1
P-OKITM07-10-320-07-PID-3709 | TM140422 | TM1404JBA102 | TM1404ASD102 | TM140422LC002 | TM140422LV002 | TM140422LV002.OUT | WARM WATER TANK LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3709 | TM140422 |  |  | TM140422TC004 | TM140422TE004 |  | WARM WATER TANK TEMPERATURE TEMPERATURE | TE | Temperature Sensor | Field
P-OKITM07-10-320-07-PID-3709 | TM140422 | TM1404JBA102 |  | TM140422TC004 | TM140422TT004 | TM140422TT004.MV | WARM WATER TANK TEMPERATURE TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [19 empty] | 1
P-OKITM07-10-320-07-PID-3709 | TM140422 | TM1404JBA102 | TM1404ASD102 | TM140422TC004 | TM140422TV004 | TM140422TV004.OUT | WARM WATER TANK TEMPERATURE TEMPERATURE CV SETPOINT | TV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1
P-OKITM07-10-320-07-PID-3709 | TM140422 | TM1404JBA102 |  | TM140422PC008 | TM140422PT008 | TM140422PT008.MV | FELT HP SHOWER PUMP 1 OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 7 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-3709 | TM140422 | TM1404JBA102 |  | TM140422PC009 | TM140422PT009 | TM140422PT009.MV | FELT HP SHOWER PUMP 2 OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 40 | Bar.g | [19 empty] | 1
COMPRESSED AIR
P-OKITM07-10-320-07-PID-4058 | TM140401 | TM1404JBA112 |  | TM140401PI002 | TM140401PT002 | TM140401PT002.MV | MILL COMPRESSED AIR PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4058 | TM140401 |  |  | TM140401HS003 | TM140401SV003 | TM140401SV003 | COMPRESSED AIR TO TM14.4 ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-4058 | TM140401 | TM1404JBS112 |  | TM140401HS003 | TM140401SV003.ZSC | TM140401SV003.GSC | COMPRESSED AIR TO TM14.4 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4058 | TM140401 | TM1404JBS112 |  | TM140401HS003 | TM140401SV003.ZSO | TM140401SV003.GSO | COMPRESSED AIR TO TM14.4 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4058 | TM140401 | TM1404JBS112 |  | TM140401HS003 | TM140401EV003 | TM140401EV003 | COMPRESSED AIR TO TM14.4 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
P-OKITM07-10-320-07-PID-4058 | TM140401 | TM1404JBA112 |  | TM140401PI004 | TM140401PT004 | TM140401PT004.MV | INSTRUMENT AIR STORAGE TANK #1 PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1
P-OKITM07-10-320-07-PID-4058 | TM140401 |  |  | TM140401HS005 | TM140401SV005 | TM140401SV005 | INSTRUMENT AIR STORAGE TANK #1 DRAIN ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 1
P-OKITM07-10-320-07-PID-4058 | TM140401 | TM1404JBS112 |  | TM140401HS005 | TM140401SV005.ZSC | TM140401SV005.GSC | INSTRUMENT AIR STORAGE TANK #1 DRAIN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-4058 | TM140401 | TM1404JBS112 |  | TM140401HS005 | TM140401SV005.ZSO | TM140401SV005.GSO | INSTRUMENT AIR STORAGE TANK #1 DRAIN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-4058 | TM140401 | TM1404JBS112 |  | TM140401HS005 | TM140401EV005 | TM140401EV005 | INSTRUMENT AIR STORAGE TANK #1 DRAIN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
NaOH SYSTEM
P-OKITM07-10-320-07-PID-3710 | TM140415 |  |  | TM140415HS013 | TM140415SV013 | TM140415SV013 | 32% NaOH TO TM14.4 ON/OFF VALVE | SV | On/Off Valve | [29 empty] | B
P-OKITM07-10-320-07-PID-3710 | TM140415 | TM1404JBS205 |  | TM140415HS013 | TM140415SV013.ZSC | TM140415SV013.GSC | 32% NaOH TO TM14.4 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1
P-OKITM07-10-320-07-PID-3710 | TM140415 | TM1404JBS205 |  | TM140415HS013 | TM140415SV013.ZSO | TM140415SV013.GSO | 32% NaOH TO TM14.4 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1
P-OKITM07-10-320-07-PID-3710 | TM140415 | TM1404JBS205 |  | TM140415HS013 | TM140415EV013 | TM140415EV013 | 32% NaOH TO TM14.4 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1
YANKEE COATING
P-OKITM07-10-320-07-PID-4057 | TM140416 | Supplier JB |  | TM140416FC001 | TM140416FE001 |  | RELEASE AGENT PUMP 1 OUTLET FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-4057 | TM140416 | Supplier JB |  | TM140416FC001 | TM140416FT001 | TM140416FT001.MV | RELEASE AGENT PUMP 1 OUTLET FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR |  |  | l / min | [19 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-4057 | TM140416 | Supplier JB |  | TM140416FI003 | TM140416FE003 |  | RELEASE AGENT PUMP 2 OUTLET FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-4057 | TM140416 | Supplier JB |  | TM140416FI003 | TM140416FT003 | TM140416FT003.MV | RELEASE AGENT PUMP 2 OUTLET FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR |  |  | l / min | [19 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-4057 | TM140416 | Supplier JB |  | TM140416FI005 | TM140416FE005 |  | RELEASE AGENT PUMP 3 OUTLET FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-4057 | TM140416 | Supplier JB |  | TM140416FI005 | TM140416FT005 | TM140416FT005.MV | RELEASE AGENT PUMP 3 OUTLET FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR |  |  | l / min | [19 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-4057 | TM140416 | Supplier JB |  | TM140416PC007 | TM140416PT007 | TM140416PT007.MV | YANKEE COATING PUMP 1&2 OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 |  | Bar.g | [19 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-4057 | TM140416 | Supplier JB |  | TM140416FI010 | TM140416FE010 |  | YANKEE COATING PUMP 1&2 OUTLET FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-4057 | TM140416 | Supplier JB |  | TM140416FI010 | TM140416FT010 | TM140416FT010.MV | YANKEE COATING PUMP 1&2 OUTLET FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR |  |  | l / min | [19 empty] | 3 | PMP | HOLD,not finalised
P-OKITM07-10-320-07-PID-4057 | TM140416 | Supplier JB |  | TM140416LI021 | TM140416LI021 | TM140416LI021.MV | COATING TANK LEVEL | LI | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 |  | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 3 |  | HOLD,not finalised
P-OKITM07-10-320-07-PID-4057 | TM140416 | Supplier JB |  | TM140416LI022 | TM140416LI022 | TM140416LI022.MV | RELEASE TANK LEVEL | LI | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 |  | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 3 |  | HOLD,not finalised
P-OKITM07-10-320-07-PID-4057 | TM140416 | Supplier JB |  | TM140416LI023 | TM140416LI023 | TM140416LI023.MV | MAP TANK LEVEL | LI | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 |  | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 3 |  | HOLD,not finalised
STEAM AND CONDENSATE SYSTEM
P-OKITM07-10-320-07-PID-3006 | TM140435 |  |  | TM140435TI001 | TM140435TE001 |  | TO YANKEE 13.5BAR STEAM TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 3 | PMP | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140435 | TM1404JBA112 |  | TM140435TI001 | TM140435TT001 | TM140435TT001.MV | TO YANKEE 13.5BAR STEAM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 350 | ˚C | [19 empty] | 3 | PMP | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140435 | TM1404JBA112 |  | TM140435PI002 | TM140435PT002 | TM140435PT002.MV | TO YANKEE 13.5BAR STEAM PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 15 | Bar.g | [19 empty] | 3 | PMP | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140435 | TM1404JBA112 |  | TM140435FI003 | TM140435FT003 | TM140435FT003.MV | TO YANKEE 13.5BAR STEAM FLOW | FT | Vortex Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 11 | t/h | [19 empty] | 3 | PMP | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140435 |  |  | TM140435TI015 | TM140435TE015 |  | TO YANKEE 20BAR STEAM TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 3 |  | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140435 | TM1404JBA112 |  | TM140435TI015 | TM140435TT015 | TM140435TT015.MV | TO YANKEE 20BAR STEAM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 3 |  | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140435 | TM1404JBA112 |  | TM140435PI016 | TM140435PT016 | TM140435PT016.MV | TO YANKEE 20BAR STEAM PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 25 | Bar.g | [19 empty] | 3 |  | Already In PMP IO List
P-OKITM07-10-320-07-PID-3006 | TM140435 | TM1404JBA112 |  | TM140435FI017 | TM140435FT017 | TM140435FT017.MV | TO YANKEE 20BAR STEAM FLOW | FT | Vortex Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6.5 | t/h | [19 empty] | 3 |  | Already In PMP IO List
Hall ventilation
P-OKITM07-10-320-08-FLD-3702 | TM140400 | TM1404JBD202 |  | TM140400PDS102 | TM140400PDS102 | TM140400PDS102.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 1
P-OKITM07-10-320-08-FLD-3702 | TM140400 | TM1404JBD202 |  | TM140400PDS103 | TM140400PDS103 | TM140400PDS103.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 1
P-OKITM07-10-320-08-FLD-3702 | TM140400 | TM1404JBD301 |  | TM140400PDS104 | TM140400PDS104 | TM140400PDS104.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 1
P-OKITM07-10-320-08-FLD-3702 | TM140400 | TM1404JBD301 |  | TM140400PDS105 | TM140400PDS105 | TM140400PDS105.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 1
P-OKITM07-10-320-08-FLD-3702 | TM140400 | TM1404JBD301 |  | TM140400PDS106 | TM140400PDS106 | TM140400PDS106.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 1
P-OKITM07-10-320-08-FLD-3702 | TM140400 | TM1404JBD301 |  | TM140400XS107 | TM140400XS107 | TM140400XS107 | TM 14.4 EXHAUST AIR FAN1 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3702 | TM140400 | TM1404JBD301 |  | TM140400XS108 | TM140400XS108 | TM140400XS108 | TM 14.4 EXHAUST AIR FAN2 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3702 | TM140400 | TM1404JBD301 |  | TM140400XS109 | TM140400XS109 | TM140400XS109 | TM 14.4 EXHAUST AIR FAN3 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3702 | TM140400 | TM1404JBD301 |  | TM140400XS110 | TM140400XS110 | TM140400XS110 | TM 14.4 EXHAUST AIR FAN4 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3702 | TM140400 | TM1404JBD301 |  | TM140400XS111 | TM140400XS111 | TM140400XS111 | TM 14.4 EXHAUST AIR FAN5 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-3702 | TM140400 | TM1404JBD301 |  | TM140400XS112 | TM140400XS112 | TM140400XS112 | TM 14.4 EXHAUST AIR FAN6 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
HVAC Air Condition
P-OKITM07-10-320-08-FLD-4051 | TM140400 | NA |  | TM140400PDS001 | TM140400PDS001 | TM140400PDS001.L | TM 14.4 TM MCC ROOM AIR FAN FILTER 1 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-4051 | TM140400 | NA |  | TM140400PDS002 | TM140400PDS002 | TM140400PDS002.L | TM 14.4 TM MCC ROOM AIR FAN FILTER 2 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-4051 | TM140400 | NA |  | TM140400PDS003 | TM140400PDS003 | TM140400PDS003.L | TM 14.4 TM MCC ROOM AIR FAN FILTER 3 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-4051 | TM140400 | NA |  | TM140400PDS004 | TM140400PDS004 | TM140400PDS004.L | TM 14.4 TM MCC ROOM AIR FAN FILTER 4 DIFFERENTIAL PRESSURE(MAU1) | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-4051 | TM140400 | NA |  | TM140400PDS005 | TM140400PDS005 | TM140400PDS005.L | TM 14.4 TM MCC ROOM AIR FAN FILTER 4 DIFFERENTIAL PRESSURE(MAU2) | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-4051 | TM140400 | NA |  | TM140400XS006 | TM140400XS006 | TM140400XS006 | TM 14.4 TM MCC ROOM AC1 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-4051 | TM140400 | NA |  | TM140400XS007 | TM140400XS007 | TM140400XS007 | TM 14.4 TM MCC ROOM AC2 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-4051 | TM140400 | NA |  | TM140400XS008 | TM140400XS008 | TM140400XS008 | TM 14.4 TM MCC ROOM AC3 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-4051 | TM140400 | NA |  | TM140400XS009 | TM140400XS009 | TM140400XS009 | TM 14.4 TM MCC ROOM AC4 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-4051 | TM140400 | NA |  | TM140400II010 | TM140400IT010 | TM140400IT010.MV | TM 14.4 TM MCC ROOM AC PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-4051 | TM140400 | NA |  | TM140400II011 | TM140400IT011 | TM140400IT011.MV | TM 14.4 SUPPLY FAN PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-4051 | TM140400 | NA |  | TM140400II012 | TM140400IT012 | TM140400IT012.MV | TM 14.4 EXHAUST FAN PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR
P-OKITM07-10-320-08-FLD-4051 | TM140400 | NA |  | TM140400TI013 | TM140400TT013 | TM140400TT013.MV | TM 14.4 TM MCC ROOM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 0 | 50 | ˚C
P-OKITM07-10-320-08-FLD-4051 | TM140400 | NA |  | TM140400MI014 | TM140400MT014 | TM140400MT014.MV | TM 14.4 TM MCC ROOM HUMIDITY | MT | Humidity Transmitter(Integrated In TT) | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 40 | 60 | %
P-OKITM07-10-320-08-FLD-4051 | TM140400 | NA |  | TM140400TI015 | TM140400TT015 | TM140400TT015.MV | TM 14.4 TM RACK ROOM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 0 | 50 | ˚C
P-OKITM07-10-320-08-FLD-4051 | TM140400 | NA |  | TM140400MI016 | TM140400MT016 | TM140400MT016.MV | TM 14.4 TM RACK ROOM HUMIDITY | MT | Humidity Transmitter(Integrated In TT) | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 40 | 60 | %

## 14.4-Exchange Communication LST
PMT: |  |  |  |  | Design Institute: |  |  | Project No. | P-OKITM07-10 | [6 empty] | EXCHANGE COMMUNICTION LIST
[8 empty] | Project Name | DETAIL ENGINEERING FOR 4(FOUR) UNITS TISSUE MACHINE
[8 empty] | Doc. No. | P-OKITM07-10-320-06-LST-4005 | [7 empty] | Abbreviations
Owner: | [7 empty] | Rev. No. | 4 |  |  | Prep'd by | Dengzuijie |  |  |  | EER Electronic Equipment Room |  |  |  | SQRT Square Root
[8 empty] | Purpose | Final |  |  | Chk'd by | Chengjianguo |  |  |  | CCR Control Center Room
[8 empty] | Date | 8,30,2021 |  |  | Appv'd by | LiXiangdong |  |  |  | ESP Electrostatic Precipitator
P&ID No. | Area | Motor Tag reference | Loop No. | Tag No. | System Tag No. | Service Description | Signal Tag | Instrument Type | Location | System | IO Type | Signal |  |  | IO Loc. | PV LO | PV HI | Eng. Unit | Alarm | [6 empty] | State "0" | State "1" | CV Fail Action | CV Ctrl Action | PV CHAR | From |  | Cable |  |  | To |  | Rev. | Supply | Remarks
[12 empty] | Type | Power | Wire |  |  |  |  | LLL | LL | L | Nor. | H | HH | HHH | [5 empty] | JB/Panel No. | TB | Cable Number | Cable Type | Cable Order | Cabinet No. | TB |  | By
MACHINE BROKE
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM140417U003 | TM140417SC025 | TM140417SX025 | TM140417SX025.PRO | BROKE INTERIM TOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM140417U001 | TM140417SC050 | TM140417SX050 | TM140417SX050.PRO | BROKE DEFLAKED CHEST PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM140417A004 | TM140417SC054 | TM140417SX054 | TM140417SX054.PRO | YANKEE PULPER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 2
P-OKITM07-10-320-07-PID-4052 | TM140417 | TM140417U002 | TM140417SC092 | TM140417SX092 | TM140417SX092.PRO | BROKE THICKENER TANK PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
STOCK APPROACH
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420U001 | TM140420SC013 | TM140420SX013 | TM140420SX013.PRO | MIXING CHEST PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420M001 | TM140420EC033 | TM140420SX013 | TM140420SX013.PRO | TICKLER REFINER POWER VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420U003 | TM140420SC046 | TM140420SX046 | TM140420SX046.PRO | SWEETENER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420U004 | TM140420SC056 | TM140420SX056 | TM140420SX056.PRO | MACHINE CHEST PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420U006 | TM140420SC071 | TM140420SX071 | TM140420SX071.PRO | FAN PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-4051 | TM140420 | TM140420U007 | TM140420SC102 | TM140420SX102 | TM140420SX102.PRO | W.W OVERFLOW CHEST PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-4051 | TM140415 |  | TM140415FC005 | TM140415FX005A | TM140415FX005A.PRO | WET STRENGHT AGENT TO MIXING CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-4051 | TM140415 |  | TM140415FC005 | TM140415FX005B | TM140415FX005B.PRO | WET STRENGHT AGENT TO MIXING CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-4051 | TM140415 |  | TM140415FC006 | TM140415FX006A | TM140415FX006A.PRO | DRY STRENGHT AGENT TO MACHINE CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-4051 | TM140415 |  | TM140415FC006 | TM140415FX006B | TM140415FX006B.PRO | DRY STRENGHT AGENT TO MACHINE CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-4051 | TM140415 |  | TM140415FC007 | TM140415FX007A | TM140415FX007A.PRO | SOFT AGENT TO MIXING CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-4051 | TM140415 |  | TM140415FC007 | TM140415FX007B | TM140415FX007B.PRO | SOFT AGENT TO MIXING CHEST PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-4051 | TM140415 |  | TM140415FC008 | TM140415FX008A | TM140415FX008A.PRO | CMC TO FAN PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
P-OKITM07-10-320-07-PID-4051 | TM140415 |  | TM140415FC008 | TM140415FX008B | TM140415FX008B.PRO | CMC TO FAN PUMP FLOW VFC SETPOINT | FX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC
WHITE WATER AND FIBRE RECOVERY
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421M001 | TM140421SC027 | TM140421SX027 | TM140421SX027.PRO | DISC FILTER MOTOR SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421U001 | TM140421SC029 | TM140421SX029 | TM140421SX029.PRO | DISC FILTER FEED PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421U002 | TM140421SC030 | TM140421SX030 | TM140421SX030.PRO | TM AREA CRC PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421U003 | TM140421SC031 | TM140421SX031 | TM140421SX031.PRO | YANKEE-TRIM PULPER & OVER FLOW PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421U007 | TM140421SC032 | TM140421SX032 | TM140421SX032.PRO | CLARIFIED TANK PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421U008 | TM140421SC033 | TM140421SX033 | TM140421SX033.PRO | DISC FILTER SHOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421U004 | TM140421SC047 | TM140421SX047 | TM140421SX047.PRO | REC PULP CHEST PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421U009 | TM140421SC048 | TM140421SX048 | TM140421SX048.PRO | CWW LP SHOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421U006 | TM140421SC049 | TM140421SX049 | TM140421SX049.PRO | CWW HP SHOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421U005 | TM140421SC051 | TM140421SX051 | TM140421SX051.PRO | CLOUDY CIRCULATION PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421U011 | TM140421SC052 | TM140421SX052 | TM140421SX052.PRO | SCWW LP SHOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | 0
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421U013 | TM140421SC142 | TM140421SX142 | TM140421SX142.PRO | SCWW HP SHOWER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-4055 | TM140421 | TM140421U012 | TM140421SC143 | TM140421SX143 | TM140421SX143.PRO | PMP DEMAND & CLEANING PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-4055 | TM140121 | TM140421U014 | TM140121SC146 | TM140121SX146 | TM140121SX146.PRO | DUST SCWW PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
FRESH WATER
P-OKITM07-10-320-07-PID-3709 | TM140422 | TM140422U008 | TM140422SC031 | TM140422SX031 | TM140422SX031.PRO | WARM WATER PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3709 | TM140422 | TM140422U009 | TM140422SC032 | TM140422SX032 | TM140422SX032.PRO | WARM WATER PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3709 | TM140422 | TM140422U010 | TM140422SC033 | TM140422SX033 | TM140422SX033.PRO | FELT HP SHOWER PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-3709 | TM140422 | TM140422U011 | TM140422SC034 | TM140422SX034 | TM140422SX034.PRO | FELT HP SHOWER PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
YANKEE COATING
P-OKITM07-10-320-07-PID-4057 | TM140416 |  | TM140416SC002 | TM140416SX002 | TM140416SX002.PRO | RELEASE AGENT PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-4057 | TM140416 |  | TM140416SC004 | TM140416SX004 | TM140416SX004.PRO | RELEASE AGENT PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-4057 | TM140416 |  | TM140416SC006 | TM140416SX006 | TM140416SX006.PRO | RELEASE AGENT PUMP 3 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-4057 | TM140416 |  | TM140416SC008 | TM140416SX008 | TM140416SX008.PRO | YANKEE COATING PUMP 1 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-320-07-PID-4057 | TM140416 |  | TM140416SC009 | TM140416SX009 | TM140416SX009.PRO | YANKEE COATING PUMP 2 SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS |  | Profibus DP |  |  | MCC | [22 empty] | B

## IO Summary
I/O COUNT SUMMARY
| AI | AO | DI | DO | TOTAL | REMARK
DCS | 118 | 45 | 195 | 78 | 436 | TM14.4 DCS
SIS | 0 | 0 | 0 | 0 | 0
SUM | 118 | 45 | 195 | 78 | 436

## Definitions
P&ID No. | The P&ID drawing number where the equipment is located.
Area | The Area where the equipment is located
Loop No. | Loop Number
Tag No. | Tag Name according to APP guideline
System Tag No. | Tag name to be appeared in DCS
Service Description | Process/service description
Signal Tag | Signal Tagname
Instrument Type | Type of instrument
Location | Location of the instrument
System | in DCS, PLC or local
IO Type | Type of input or output
Signal - Type | Signal type
Signal - Power | Power for the signal
Signal - Wire | wiring configuration
IO Loc. | Input and Output location
PV LO | Range Low
PV HI | Range High
Eng. Unit | Engineering Unit
Alarm | LLL- Low Low Low, HHH- High High High etc
State "0" | For Valves, If signal is zero, what willl be the valve opening.
State "1" | For Valves, If signal is one, what willl be the valve opening.
CV fail Action | For Valves, If air fails, what willl be the valve status.
CV Control Action | For Valves, Direction of the control.
PV CHAR | Process value characteristics
Rev | Revision
Supply By | Supplier name
Remarks