## Converting
PMT: | [5 empty] | Design Institute: |  |  | Project No. | P-OKITM07-10 | [6 empty] | DCS I/O Database
[9 empty] | Project Name | DETAIL ENGINEERING FOR 4(FOUR) UNITS TISSUE MACHINE
[9 empty] | Doc. No. | P-OKITM07-10-500-06-LST-4405 | [7 empty] | Abbreviations
Owner: | [8 empty] | Rev. No. | 6 |  |  | Prep'd by | Dengzuijie |  |  |  | EER Electronic Equipment Room |  |  |  | SQRT Square Root
[9 empty] | Purpose | Final |  |  | Chk'd by | Chengjianguo |  |  |  | CCR Control Center Room
[9 empty] | Date | 30,8,2021 |  |  | Appv'd by | LiXiangdong |  |  |  | ESP Electrostatic Precipitator
P&ID No. | Area |  |  | Loop No. | Tag No. | System Tag No. | Service Description | Signal Tag | Instrument Type | Location | System | IO Type | Signal |  |  | IO Loc. | PV LO | PV HI | Eng. Unit | Alarm | [6 empty] | State "0" | State "1" | CV Fail Action | CV Ctrl Action | PV CHAR | From |  | Cable |  |  | To |  | Rev. | Supply | Remarks
[13 empty] | Type | Power | Wire |  |  |  |  | LLL | LL | L | Nor. | H | HH | HHH | [5 empty] | JB/Panel No. | TB | Cable Number | Cable Type | Cable Order | Cabinet No. | TB |  | By
CONVERTING MILL BROKE
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBA001 |  | TM140517LC001 | TM140517LT001 | TM140517LT001.MV | FINISHING PULPER LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 2500 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBA001 | TM1405ASD001 | TM140517LC001 | TM140517LV001A | TM140517LV001A.OUT | FINISHING PULPER LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBA001 | TM1405ASD001 | TM140517LC001 | TM140517LV001B | TM140517LV001B.OUT | FINISHING PULPER LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBA001 |  | TM140517NC002 | TM140517NE002 |  | FINISHING PULPER PUMP OUTLET CONSISTENCY | NE | Blade Consistency Sensor | Field | [28 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBA001 |  | TM140517NC002 | TM140517NT002 | TM140517NT002.MV | FINISHING PULPER PUMP OUTLET CONSISTENCY | NT | Blade Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 6 | %Cs | [19 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS003 | TM140517SV003 | TM140517SV003 | FINISHING PULPER PUMP INLET ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS003 | TM140517SV003.ZSC | TM140517SV003.GSC | FINISHING PULPER PUMP INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS003 | TM140517SV003.ZSO | TM140517SV003.GSO | FINISHING PULPER PUMP INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS003 | TM140517EV003 | TM140517EV003 | FINISHING PULPER PUMP INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBA001 |  | TM140517FC004 | TM140517FE004 |  | WHITE WATER TO FINISHING PULPER FLOW | FE | Magnetic Flow Sensor | Field | DCS | [27 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBA001 |  | TM140517FC004 | TM140517FT004 | TM140517FT004.MV | WHITE WATER TO FINISHING PULPER FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1700 | l/min | [19 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBA001 |  | TM140517FC004 | TM140517FV004 | TM140517FV004.OUT | WHITE WATER TO FINISHING PULPER FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS005 | TM140517SV005 | TM140517SV005 | SEALING WATER TO FINISHING PULPER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS005 | TM140517SV005.ZSC | TM140517SV005.GSC | SEALING WATER TO FINISHING PULPER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS005 | TM140517SV005.ZSO | TM140517SV005.GSO | SEALING WATER TO FINISHING PULPER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS005 | TM140517EV005 | TM140517EV005 | SEALING WATER TO FINISHING PULPER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBD001 |  | TM140517FS006 | TM140517FS006 | TM140517FS006.L | SEALING WATER TO FINISHING PULPER AGITATOR FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 5 | Andritz | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBD001 |  | TM140517FS007 | TM140517FS007 | TM140517FS007.L | SEALING WATER TO FINISHING PULPER LEVEL TRANSMITTER FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBD001 |  | TM140517FS008 | TM140517FS008 | TM140517FS008.L | SEALING WATER TO FINISHING PULPER PUMP FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Flow L | Not Flow L | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 |  |  | TM140517WC010 | TM140517WE010 |  | FINISHING PULPER PRODUCTION | WE | Weight Sensor | Field | DCS | [27 empty] | 6 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 |  |  | TM140517WC010 | TM140517WT010 | TM140517WT010.MV | FINISHING PULPER PRODUCTION | WT | Weight Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 1700 | t | [19 empty] | 6 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBD001 |  | TM140517SS011 | TM140517SS011 | TM140517SS011.L | BROKE CONVEYORSPEED LOW | SS | Speed Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Speed Low | Not Speed Low | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 |  |  | TM140517XS013 | TM140517CP01 | TM1400111CP01 | BALE RECIEVING CONVEYOR LOCAL CONTROL PANEL | [31 empty] | 6 | Andritz | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM140517CP01 |  | TM140517XS013 | TM140517S11.1 013 | TM140517S11.1 013.TEST | LAMP TEST | S11.1 | Push Button | +CP01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 6 | Andritz | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM140517CP01 |  | TM140517XS013 | TM140517S11.2 013 | TM140517S11.2 013.FLT | FAULT ACKNOWLEDGE | S11.2 | Push Button | +CP01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 6 | Andritz | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM140517CP01 |  | TM140517XS013 | TM140517S11.3 013 | TM140517S11.3 013.FWD | LOCAL START FWD | S11.3 | Push Button | +CP01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 6 | Andritz | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM140517CP01 |  | TM140517XS013 | TM140517S11.4 013 | TM140517S11.4 013.REV | LOCAL START REV | S11.4 | Push Button | +CP01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 6 | Andritz | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM140517CP01 |  | TM140517XS013 | TM140517S11.5 013 | TM140517S11.5 013.L/M | LOCAL/DCS | S11.5 | Select Switch | +CP01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 6 | Andritz | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM140517CP01 |  | TM140517XS013 | TM140517S11.6 013 | TM140517S11.6 013.RDY | BALE REALDY | S11.6 | Push Button | +CP01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 6 | Andritz | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM140517CP01 |  | TM140517XS013 | TM140517S11.7 013 | TM140517S11.7 013.RDYL | BALE READY LAMP | S11.7 | Indicator light | +CP01 | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 6 | Andritz | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM140517CP01 |  | TM140517XS013 | TM140517S11.8 013 | TM140517S11.8 013.FWDL | RUN FW LAMP | S11.8 | Indicator light | +CP01 | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 6 | Andritz | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM140517CP01 |  | TM140517XS013 | TM140517S11.9 013 | TM140517S11.9 013.REVL | RUN REV LAMP | S11.9 | Indicator light | +CP01 | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 6 | Andritz | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM140517CP01 |  | TM140517XS014 | TM140517S10 014 | TM140517S10 014.ESTOP | BALE RECIEVING CONVEYOR E-STOP | S10 | E-STOP Push Button | +CP01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | E-Stop | [11 empty] | 6 | Andritz | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBA001 |  | TM140517FC015 | TM140517FE015 |  | FINISHING PULPER PUMP INLET DILUTION WATER FLOW | FE | Magnetic Flow Sensor | Field | DCS | [27 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBA001 |  | TM140517FC015 | TM140517FT015 | TM140517FT015.MV | FINISHING PULPER PUMP INLET DILUTION WATER FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230 VAC | 2+3 | RR | 0 | 700 | l/min | [19 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBA001 |  | TM140517FC015 | TM140517FV015 | TM140517FV015.OUT | FINISHING PULPER PUMP INLET DILUTION WATER FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBA001 |  | TM140517PC017 | TM140517PT017 | TM140517PT017.MV | FINISHING PULPER PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS002 |  | TM140517HS021 | TM140517SV021 | TM140517SV021 | FINISHING PULPER PUMP TO TM14.1 BROKE INTERIM TOWER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS002 |  | TM140517HS021 | TM140517SV021.ZSC | TM140517SV021.GSC | FINISHING PULPER PUMP TO TM14.1 BROKE INTERIM TOWER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS002 |  | TM140517HS021 | TM140517SV021.ZSO | TM140517SV021.GSO | FINISHING PULPER PUMP TO TM14.1 BROKE INTERIM TOWER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS002 |  | TM140517HS021 | TM140517EV021 | TM140517EV021 | FINISHING PULPER PUMP TO TM14.1 BROKE INTERIM TOWER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS002 |  | TM140517HS022 | TM140517SV022 | TM140517SV022 | FINISHING PULPER PUMP TO TM14.3 BROKE INTERIM TOWER ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS002 |  | TM140517HS022 | TM140517SV022.ZSC | TM140517SV022.GSC | FINISHING PULPER PUMP TO TM14.3 BROKE INTERIM TOWER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS002 |  | TM140517HS022 | TM140517SV022.ZSO | TM140517SV022.GSO | FINISHING PULPER PUMP TO TM14.3 BROKE INTERIM TOWER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS002 |  | TM140517HS022 | TM140517EV022 | TM140517EV022 | FINISHING PULPER PUMP TO TM14.3 BROKE INTERIM TOWER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS023 | TM140517SV023 | TM140517SV023 | TM14.1 SEALING WATER TO FINISHING BROKE SCREEN ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS023 | TM140517SV023.ZSC | TM140517SV023.GSC | TM14.1 SEALING WATER TO FINISHING BROKE SCREEN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS023 | TM140517SV023.ZSO | TM140517SV023.GSO | TM14.1 SEALING WATER TO FINISHING BROKE SCREEN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS023 | TM140517EV023 | TM140517EV023 | TM14.1 SEALING WATER TO FINISHING BROKE SCREEN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS024 | TM140517SV024 | TM140517SV024 | TM14.3 SEALING WATER TO FINISHING BROKE SCREEN ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS024 | TM140517SV024.ZSC | TM140517SV024.GSC | TM14.3 SEALING WATER TO FINISHING BROKE SCREEN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS024 | TM140517SV024.ZSO | TM140517SV024.GSO | TM14.3 SEALING WATER TO FINISHING BROKE SCREEN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS024 | TM140517EV024 | TM140517EV024 | TM14.3 SEALING WATER TO FINISHING BROKE SCREEN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS025 | TM140517SV025 | TM140517SV025 | TM14.1 YANKEE&OVER FLOW PUMP WATER TO FINISHING BROKE SCREEN ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS025 | TM140517SV025.ZSC | TM140517SV025.GSC | TM14.1 YANKEE&OVER FLOW PUMP WATER TO FINISHING BROKE SCREEN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS025 | TM140517SV025.ZSO | TM140517SV025.GSO | TM14.1 YANKEE&OVER FLOW PUMP WATER TO FINISHING BROKE SCREEN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS025 | TM140517EV025 | TM140517EV025 | TM14.1 YANKEE&OVER FLOW PUMP WATER TO FINISHING BROKE SCREEN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS026 | TM140517SV026 | TM140517SV026 | TM14.3 YANKEE&OVER FLOW PUMP WATER TO FINISHING BROKE SCREEN ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS026 | TM140517SV026.ZSC | TM140517SV026.GSC | TM14.3 YANKEE&OVER FLOW PUMP WATER TO FINISHING BROKE SCREEN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS026 | TM140517SV026.ZSO | TM140517SV026.GSO | TM14.3 YANKEE&OVER FLOW PUMP WATER TO FINISHING BROKE SCREEN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM1405JBS001 |  | TM140517HS026 | TM140517EV026 | TM140517EV026 | TM14.3 YANKEE&OVER FLOW PUMP WATER TO FINISHING BROKE SCREEN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 5 |  | Converting Mill to SP2
COMPRESSED AIR
P-OKITM07-10-500-03-PID-4402 | TM140501 | TM1403JBA103 |  | TM140501PI001 | TM140501PT001 | TM140501PT001.MV | INSTRUMENT AIR STORAGE TANK #2 PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-500-03-PID-4402 | TM140501 | TM1405JBS003 |  | TM140501HS002 | TM140501SV002 | TM140501SV002 | INSTRUMENT AIR STORAGE TANK #2 DRAIN ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-500-03-PID-4402 | TM140501 | TM1405JBS003 |  | TM140501HS002 | TM140501SV002.ZSC | TM140501SV002.GSC | INSTRUMENT AIR STORAGE TANK #2 DRAIN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-500-03-PID-4402 | TM140501 | TM1405JBS003 |  | TM140501HS002 | TM140501SV002.ZSO | TM140501SV002.GSO | INSTRUMENT AIR STORAGE TANK #2 DRAIN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-500-03-PID-4402 | TM140501 | TM1405JBS003 |  | TM140501HS002 | TM140501EV002 | TM140501EV002 | INSTRUMENT AIR STORAGE TANK #2 DRAIN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-500-03-PID-4402 | TM140501 | TM1403JBA103 |  | TM140501PI011 | TM140501PT011 | TM140501PT011.MV | INSTRUMENT AIR STORAGE TANK #2 PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-500-03-PID-4402 | TM140501 | TM1405JBS003 |  | TM140501HS012 | TM140501SV012 | TM140501SV012 | INSTRUMENT AIR STORAGE TANK #2 DRAIN ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-500-03-PID-4402 | TM140501 | TM1405JBS003 |  | TM140501HS012 | TM140501SV012.ZSC | TM140501SV012.GSC | INSTRUMENT AIR STORAGE TANK #2 DRAIN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-500-03-PID-4402 | TM140501 | TM1405JBS003 |  | TM140501HS012 | TM140501SV012.ZSO | TM140501SV012.GSO | INSTRUMENT AIR STORAGE TANK #2 DRAIN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-500-03-PID-4402 | TM140501 | TM1405JBS003 |  | TM140501HS012 | TM140501EV012 | TM140501EV012 | INSTRUMENT AIR STORAGE TANK #2 DRAIN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-500-03-PID-4402 | TM140601 | TM1405JBA002 |  | TM140601PI001 | TM140601PT001 | TM140601PT001.MV | INSTRUMENT AIR STORAGE TANK #2 PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 5 |  | Auto-Warehouse Mill to SP2
P-OKITM07-10-500-03-PID-4402 | TM140601 |  |  | TM140601HS002 | TM140601SV002 | TM140601SV002 | INSTRUMENT AIR STORAGE TANK #2 DRAIN ON/OFF VALVE | SV | On/Off Valve | [29 empty] | 5 |  | Auto-Warehouse Mill to SP2
P-OKITM07-10-500-03-PID-4402 | TM140601 | TM1406JBS001 |  | TM140601HS002 | TM140601SV002.ZSC | TM140601SV002.GSC | INSTRUMENT AIR STORAGE TANK #2 DRAIN ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 5 |  | Auto-Warehouse Mill to SP2
P-OKITM07-10-500-03-PID-4402 | TM140601 | TM1406JBS001 |  | TM140601HS002 | TM140601SV002.ZSO | TM140601SV002.GSO | INSTRUMENT AIR STORAGE TANK #2 DRAIN ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 5 |  | Auto-Warehouse Mill to SP2
P-OKITM07-10-500-03-PID-4402 | TM140601 | TM1406JBS001 |  | TM140601HS002 | TM140601EV002 | TM140601EV002 | INSTRUMENT AIR STORAGE TANK #2 DRAIN ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 5 |  | Auto-Warehouse Mill to SP2
STEAM AND CONDENSATE SYSTEM
P-OKITM07-10-500-08-FLD--4402 | TM140535 | TM1403JBA112 |  | TM140535PI001 | TM140535PT001 | TM140535PT001.MV | 13.5 BAR STEAM BEFORE PRDS PRESSURE | PT | Pressure Transmitter | Field | PRDS PLC | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 16 | Bar.g | [19 empty] | 5 | PRDS Supplier | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4402 | TM140535 |  |  | TM140535TI002 | TM140535TE002 |  | 13.5 BAR STEAM BEFORE TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 5 | PRDS Supplier | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4402 | TM140535 | TM1403JBA112 |  | TM140535TI002 | TM140535TT002 | TM140535TT002.MV | 13.5 BAR STEAM BEFORE TEMPERATURE | TT | Temperature Transmitter | Field | PRDS PLC | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 300 | ˚C | [19 empty] | 5 | PRDS Supplier | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4402 | TM140535 | TM1403JBA112 |  | TM140535PC003 | TM140535PT003 | TM140535PT003.MV | PRDS PRESSURE | PT | Pressure Transmitter | Field | PRDS PLC | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 5 | PRDS Supplier | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4402 | TM140535 | TM1403JBA112 | TM1403ASD112 | TM140535PC003 | TM140535PV003 | TM140535PV003.OUT | PRDS PRESSURE CV SETPOINT | PV | Control Valve | Field | PRDS PLC | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 5 | PRDS Supplier | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4402 | TM140535 |  |  | TM140535TC004 | TM140535TE004 |  | PRDS TEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | 5 | PRDS Supplier | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4402 | TM140535 | TM1403JBA112 |  | TM140535TC004 | TM140535TT004 | TM140535TT004.MV | PRDS TEMPERATURE | TT | Temperature Transmitter | Field | PRDS PLC | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 200 | ˚C | [19 empty] | 5 | PRDS Supplier | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4402 | TM140535 | TM1403JBA112 | TM1403ASD112 | TM140535TC004 | TM140535TV004 | TM140535TV004.OUT | PRDS TEMPERATURE CV SETPOINT | TV | Control Valve | Field | PRDS PLC | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 5 | PRDS Supplier | Converting Mill to SP2
CVT Hall ventilation
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD002 |  | TM140500PDS241 | TM140500PDS241 | TM140500PDS241.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD002 |  | TM140500PDS242 | TM140500PDS242 | TM140500PDS242.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD002 |  | TM140500PDS243 | TM140500PDS243 | TM140500PDS243.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD002 |  | TM140500PDS244 | TM140500PDS244 | TM140500PDS244.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD002 |  | TM140500PDS245 | TM140500PDS245 | TM140500PDS245.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD002 |  | TM140500PDS246 | TM140500PDS246 | TM140500PDS246.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD002 |  | TM140500PDS247 | TM140500PDS247 | TM140500PDS247.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD002 |  | TM140500PDS248 | TM140500PDS248 | TM140500PDS248.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD002 |  | TM140500PDS249 | TM140500PDS249 | TM140500PDS249.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD002 |  | TM140500PDS250 | TM140500PDS250 | TM140500PDS250.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD002 |  | TM140500PDS251 | TM140500PDS251 | TM140500PDS251.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD002 |  | TM140500PDS252 | TM140500PDS252 | TM140500PDS252.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD002 |  | TM140500PDS253 | TM140500PDS253 | TM140500PDS253.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD002 |  | TM140500PDS254 | TM140500PDS254 | TM140500PDS254.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD002 |  | TM140500PDS255 | TM140500PDS255 | TM140500PDS255.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD003 |  | TM140500PDS256 | TM140500PDS256 | TM140500PDS256.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD003 |  | TM140500PDS257 | TM140500PDS257 | TM140500PDS257.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD003 |  | TM140500PDS258 | TM140500PDS258 | TM140500PDS258.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD003 |  | TM140500PDS259 | TM140500PDS259 | TM140500PDS259.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD003 |  | TM140500PDS260 | TM140500PDS260 | TM140500PDS260.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD004 |  | TM140500PDS261 | TM140500PDS261 | TM140500PDS261.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD004 |  | TM140500PDS262 | TM140500PDS262 | TM140500PDS262.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD004 |  | TM140500PDS263 | TM140500PDS263 | TM140500PDS263.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD004 |  | TM140500PDS264 | TM140500PDS264 | TM140500PDS264.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD004 |  | TM140500PDS265 | TM140500PDS265 | TM140500PDS265.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD004 |  | TM140500PDS266 | TM140500PDS266 | TM140500PDS266.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD004 |  | TM140500PDS267 | TM140500PDS267 | TM140500PDS267.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD004 |  | TM140500PDS268 | TM140500PDS268 | TM140500PDS268.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD004 |  | TM140500PDS269 | TM140500PDS269 | TM140500PDS269.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD004 |  | TM140500PDS270 | TM140500PDS270 | TM140500PDS270.L | SUPPLY AIR UNIT DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 50 | KPa.g | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD005 |  | TM140500XS201 | TM140500XS201 | TM140500XS201 | CONVERTING EXHAUST AIR FAN1 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD005 |  | TM140500XS202 | TM140500XS202 | TM140500XS202 | CONVERTING EXHAUST AIR FAN2 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD005 |  | TM140500XS203 | TM140500XS203 | TM140500XS203 | CONVERTING EXHAUST AIR FAN3 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD005 |  | TM140500XS204 | TM140500XS204 | TM140500XS204 | CONVERTING EXHAUST AIR FAN4 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD005 |  | TM140500XS205 | TM140500XS205 | TM140500XS205 | CONVERTING EXHAUST AIR FAN5 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD005 |  | TM140500XS206 | TM140500XS206 | TM140500XS206 | CONVERTING EXHAUST AIR FAN6 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD005 |  | TM140500XS207 | TM140500XS207 | TM140500XS207 | CONVERTING EXHAUST AIR FAN7 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD005 |  | TM140500XS208 | TM140500XS208 | TM140500XS208 | CONVERTING EXHAUST AIR FAN8 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD005 |  | TM140500XS209 | TM140500XS209 | TM140500XS209 | CONVERTING EXHAUST AIR FAN9 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD005 |  | TM140500XS210 | TM140500XS210 | TM140500XS210 | CONVERTING EXHAUST AIR FAN10 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD005 |  | TM140500XS211 | TM140500XS211 | TM140500XS211 | CONVERTING EXHAUST AIR FAN11 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD005 |  | TM140500XS212 | TM140500XS212 | TM140500XS212 | CONVERTING EXHAUST AIR FAN12 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD--4401 | TM140500 | TM1405JBD005 |  | TM140500XS213 | TM140500XS213 | TM140500XS213 | CONVERTING EXHAUST AIR FAN13 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
CVT HVAC Air Condition
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD006 |  | TM140500PDS001 | TM140500PDS001 | TM140500PDS001.L | CONVERTING AIR FAN FILTER 1 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD006 |  | TM140500PDS002 | TM140500PDS002 | TM140500PDS002.L | CONVERTING AIR FAN FILTER 2 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD006 |  | TM140500PDS003 | TM140500PDS003 | TM140500PDS003.L | CONVERTING AIR FAN FILTER 3 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD006 |  | TM140500PDS004 | TM140500PDS004 | TM140500PDS004.L | CONVERTING AIR FAN FILTER 4 DIFFERENTIAL PRESSURE(MAU1) | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD006 |  | TM140500PDS005 | TM140500PDS005 | TM140500PDS005.L | CONVERTING AIR FAN FILTER 4 DIFFERENTIAL PRESSURE(MAU2) | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD006 |  | TM140500XS011 | TM140500XS011 | TM140500XS011 | CONVERTING MCC ROOM AC1 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD006 |  | TM140500XS012 | TM140500XS012 | TM140500XS012 | CONVERTING MCC ROOM AC2 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD006 |  | TM140500XS013 | TM140500XS013 | TM140500XS013 | CONVERTING MCC ROOM AC3 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD006 |  | TM140500XS014 | TM140500XS014 | TM140500XS014 | CONVERTING MCC ROOM AC4 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD007 |  | TM140500XS015 | TM140500XS015 | TM140500XS015 | Chiller Station MCC ROOM AC1 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD007 |  | TM140500XS016 | TM140500XS016 | TM140500XS016 | Cooling Tower MCC ROOM AC2 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD007 |  | TM140500XS017 | TM140500XS017 | TM140500XS017 | PACKAGING AREA AC1 ON-OFF SWITCH SIGNAL 01 (AHU1) | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD007 |  | TM140500XS018 | TM140500XS018 | TM140500XS018 | PACKAGING AREA AC2 ON-OFF SWITCH SIGNAL 01 (AHU2) | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD007 |  | TM140500XS019 | TM140500XS019 | TM140500XS019 | PACKAGING AREA AC3 ON-OFF SWITCH SIGNAL 01 (AHU3) | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD007 |  | TM140500XS020 | TM140500XS020 | TM140500XS020 | PACKAGING AREA AC4 ON-OFF SWITCH SIGNAL 01 (AHU4) | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD008 |  | TM140500XS021 | TM140500XS021 | TM140500XS021 | PACKAGING AREA AC5 ON-OFF SWITCH SIGNAL 01 (AHU5) | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD008 |  | TM140500XS022 | TM140500XS022 | TM140500XS022 | PACKAGING AREA AC6 ON-OFF SWITCH SIGNAL 01 (AHU6) | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD008 |  | TM140500XS023 | TM140500XS023 | TM140500XS023 | PACKAGING AREA AC7 ON-OFF SWITCH SIGNAL 01 (AHU7) | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD008 |  | TM140500XS024 | TM140500XS024 | TM140500XS024 | PACKAGING AREA AC8 ON-OFF SWITCH SIGNAL 01 (AHU8) | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD008 |  | TM140500XS025 | TM140500XS025 | TM140500XS025 | PACKAGING AREA AC9 ON-OFF SWITCH SIGNAL 01 (AHU9) | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD008 |  | TM140500XS026 | TM140500XS026 | TM140500XS026 | PACKAGING AREA AC10 ON-OFF SWITCH SIGNAL 01 (AHU10) | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD008 |  | TM140500XS027 | TM140500XS027 | TM140500XS027 | PACKAGING AREA AC11 ON-OFF SWITCH SIGNAL 01 (AHU11) | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD008 |  | TM140500XS028 | TM140500XS028 | TM140500XS028 | PACKAGING AREA AC12 ON-OFF SWITCH SIGNAL 01 (AHU12) | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD008 |  | TM140500XS029 | TM140500XS029 | TM140500XS029 | PACKAGING AREA AC13 ON-OFF SWITCH SIGNAL 01 (MAU1) | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD008 |  | TM140500XS030 | TM140500XS030 | TM140500XS030 | PACKAGING AREA AC14 ON-OFF SWITCH SIGNAL 01 (MAU2) | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD008 |  | TM140500XS031 | TM140500XS031 | TM140500XS031 | PACKAGING AREA AC15 ON-OFF SWITCH SIGNAL 01 (MAU3) | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD008 |  | TM140500XS032 | TM140500XS032 | TM140500XS032 | PACKAGING AREA AC16 ON-OFF SWITCH SIGNAL 01 (MAU4) | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD008 |  | TM140500XS033 | TM140500XS033 | TM140500XS033 | PACKAGING AREA AC17 ON-OFF SWITCH SIGNAL 01 (MAU5) | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD008 |  | TM140500XS034 | TM140500XS034 | TM140500XS034 | PACKAGING AREA AC18 ON-OFF SWITCH SIGNAL 01 (MAU6) | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD007 |  | TM140500XS035 | TM140500XS035 | TM140500XS035 | VACUUM PUMP MCC ROOM AC1 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBD007 |  | TM140500XS036 | TM140500XS036 | TM140500XS036 | VACUUM PUMP MCC ROOM AC2 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBA002 |  | TM140500II021 | TM140500IT021 | TM140500IT021.MV | CONVERTING MCC ROOM AC PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBA003 |  | TM140500II022 | TM140500IT022 | TM140500IT022.MV | CONVEYOR ROOM AC PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBA003 |  | TM140500II023 | TM140500IT023 | TM140500IT023.MV | VACUUM PUMP ROOM AC PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBA003 |  | TM140500II024 | TM140500IT024 | TM140500IT024.MV | PACKAGING HALL AC PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBA003 |  | TM140500II025 | TM140500IT025 | TM140500IT025.MV | CONVERTING HALL SUPPLY FAN PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBA003 |  | TM140500II026 | TM140500IT026 | TM140500IT026.MV | CONVERTING HALL EXHAUST FAN PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBA002 |  | TM140500TI031 | TM140500TT031 | TM140500TT031.MV | CONVERTING MCC ROOM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 0 | 50 | ˚C | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBA002 |  | TM140500MI032 | TM140500MT032 | TM140500MT032.MV | CONVERTING MCC ROOM HUMIDITY | MT | Humidity Transmitter(Integrated In TT) | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 40 | 60 | % | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBA003 |  | TM140500TI033 | TM140500TT033 | TM140500TT033.MV | CONVEYOR MCC ROOM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 0 | 50 | ˚C | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBA003 |  | TM140500MI034 | TM140500MT034 | TM140500MT034.MV | CONVEYOR MCC ROOM HUMIDITY | MT | Humidity Transmitter(Integrated In TT) | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 40 | 60 | % | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBA003 |  | TM140500TI035 | TM140500TT035 | TM140500TT035.MV | VACUUM PUMP MCC ROOM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 0 | 50 | ˚C | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBA003 |  | TM140500MI036 | TM140500MT036 | TM140500MT036.MV | VACUUM PUMP MCC ROOM HUMIDITY | MT | Humidity Transmitter(Integrated In TT) | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 40 | 60 | % | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBA003 |  | TM140500TI037 | TM140500TT037 | TM140500TT037.MV | PACKAGING HALL AC PANEL TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 0 | 50 | ˚C | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-302-08-FLD-4641 | TM140500 | TM1405JBA003 |  | TM140500MI038 | TM140500MT038 | TM140500MT038.MV | PACKAGING HALL AC PANEL HUMIDITY | MT | Humidity Transmitter(Integrated In TT) | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 40 | 60 | % | [19 empty] | 5 | HVAC VENDOR | Converting Mill to SP2
P-OKITM07-10-500-08-FLD-4402 | TM140500 | TM140500CP01 |  | TM140500XS101 | TM140500S1.101 | TM140500S1.101 | COOLING WATER FILTER LOCAL PANEL | S1 | Differential Pressure High alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-500-08-FLD-4402 | TM140500 | TM140500CP01 |  | TM140500XS101 | TM140500S2.101 | TM140500S2.101 | COOLING WATER FILTER LOCAL PANEL | S2 | Flush alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-500-08-FLD-4402 | TM140500 | TM140500CP01 |  | TM140500XS101 | TM140500S3.101 | TM140500S3.101 | COOLING WATER FILTER LOCAL PANEL | S3 | Power Failure alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 |  | Converting Mill to SP2
P-OKITM07-10-500-08-FLD-4402 | TM140500 | TM1405JBA003 |  | TM140500LIS102 | TM140500LT102 | TM140500LT102.MV | COOLING TOWER LEVEL | LT | Radar Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 4200 | mm |  | 10% | 15% |  | 90% | 95% | [13 empty] | 1 |  | Converting Mill to SP2
P-OKITM07-10-500-08-FLD-4402 | TM140500 | TM1405JBD007 |  | TM140500XISA103 | TM140500XS103 | TM140500XS103.HH | COOLING TOWER 1 PUMP 1 VIBRATION HIGH | XS | Vibration Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  | Converting Mill to SP2
P-OKITM07-10-500-08-FLD-4402 | TM140500 | TM1405JBD007 |  | TM140500XISA104 | TM140500XS104 | TM140500XS104.HH | COOLING TOWER 1 PUMP 1 VIBRATION HIGH | XS | Vibration Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  | Converting Mill to SP2
AUTO-WAREHOUSE HVAC Air Condition
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBD001 |  | TM140600PDS001 | TM140600PDS001 | TM140600PDS001.L | AUTO-WAREHOUSE 1 AIR FAN FILTER 1 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.1
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBD001 |  | TM140600PDS002 | TM140600PDS002 | TM140600PDS002.L | AUTO-WAREHOUSE 1 AIR FAN FILTER 2 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.1
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBD001 |  | TM140600PDS003 | TM140600PDS003 | TM140600PDS003.L | AUTO-WAREHOUSE 1 AIR FAN FILTER 3 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 6 | HVAC VENDOR | Auto-Warehouse to TM14.1
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBD001 |  | TM140600PDS004 | TM140600PDS004 | TM140600PDS004.L | AUTO-WAREHOUSE 1 AIR FAN FILTER 4 DIFFERENTIAL PRESSURE(MAU) | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.1
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBD002 |  | TM140600PDS005 | TM140600PDS005 | TM140600PDS005.L | AUTO-WAREHOUSE 2 AIR FAN FILTER 1 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.4
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBD002 |  | TM140600PDS006 | TM140600PDS006 | TM140600PDS006.L | AUTO-WAREHOUSE 2 AIR FAN FILTER 2 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.4
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBD002 |  | TM140600PDS007 | TM140600PDS007 | TM140600PDS007.L | AUTO-WAREHOUSE 2 AIR FAN FILTER 3 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 6 | HVAC VENDOR | Auto-Warehouse to TM14.4
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBD002 |  | TM140600PDS008 | TM140600PDS008 | TM140600PDS008.L | AUTO-WAREHOUSE 2 AIR FAN FILTER 4 DIFFERENTIAL PRESSURE(MAU) | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.4
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBD001 |  | TM140600XS011 | TM140600XS011 | TM140600XS011 | AUTO-WAREHOUSE MCC ROOM 1 AC1 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.1
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBD001 |  | TM140600XS012 | TM140600XS012 | TM140600XS012 | AUTO-WAREHOUSE MCC ROOM 1 AC2 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.1
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBD001 |  | TM140600XS014 | TM140600XS014 | TM140600XS014 | AUTO-WAREHOUSE MCC ROOM 1 AC4 ON-OFF SWITCH(MAU) | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.1
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBD002 |  | TM140600XS015 | TM140600XS015 | TM140600XS015 | AUTO-WAREHOUSE MCC ROOM 2 AC1 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.4
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBD002 |  | TM140600XS016 | TM140600XS016 | TM140600XS016 | AUTO-WAREHOUSE MCC ROOM 2 AC2 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.4
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBD002 |  | TM140600XS018 | TM140600XS018 | TM140600XS018 | AUTO-WAREHOUSE MCC ROOM 2 AC4 ON-OFF SWITCH(MAU) | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.4
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBD002 |  | TM140600XS019 | TM140600XS019 | TM140600XS019 | AUTO-WAREHOUSE MCC ROOM 3 AC1 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.4
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBD002 |  | TM140600XS020 | TM140600XS020 | TM140600XS020 | AUTO-WAREHOUSE MCC ROOM 3 AC2 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.4
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBD002 |  | TM140600XS021 | TM140600XS021 | TM140600XS021 | AUTO-WAREHOUSE MCC ROOM 3 AC3 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 6 | HVAC VENDOR | Auto-Warehouse to TM14.4
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBA001 |  | TM140600II022 | TM140600IT022 | TM140600IT022.MV | WAREHOUSE MCC ROOM 1 AC PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.1
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBA002 |  | TM140600II023 | TM140600IT023 | TM140600IT023.MV | WAREHOUSE MCC ROOM 2 AC PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.4
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBA002 |  | TM140600II024 | TM140600IT024 | TM140600IT024.MV | WAREHOUSE MCC ROOM 3 AC PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | [22 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.4
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBA001 |  | TM140600TI031 | TM140600TT031 | TM140600TT031.MV | WAREHOUSE MCC ROOM 1 TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 0 | 50 | ˚C | [19 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.1
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBA001 |  | TM140600MI032 | TM140600MT032 | TM140600MT032.MV | WAREHOUSE MCC ROOM 1 HUMIDITY | MT | Humidity Transmitter(Integrated In TT) | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 40 | 60 | % | [19 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.1
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBA001 |  | TM140600TI033 | TM140600TT033 | TM140600TT033.MV | WAREHOUSE CONTROL ROOM 1 TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 0 | 50 | ˚C | [19 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.1
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBA001 |  | TM140600MI034 | TM140600MT034 | TM140600MT034.MV | WAREHOUSE CONTROL ROOM 1 HUMIDITY | MT | Humidity Transmitter(Integrated In TT) | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 40 | 60 | % | [19 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.1
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBA002 |  | TM140600TI035 | TM140600TT035 | TM140600TT035.MV | WAREHOUSE MCC ROOM 2 TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 0 | 50 | ˚C | [19 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.4
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBA002 |  | TM140600MI036 | TM140600MT036 | TM140600MT036.MV | WAREHOUSE MCC ROOM 2 HUMIDITY | MT | Humidity Transmitter(Integrated In TT) | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 40 | 60 | % | [19 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.4
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBA002 |  | TM140600TI037 | TM140600TT037 | TM140600TT037.MV | WAREHOUSE CONTROL ROOM 2 TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 0 | 50 | ˚C | [19 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.4
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBA002 |  | TM140600MI038 | TM140600MT038 | TM140600MT038.MV | WAREHOUSE CONTROL ROOM 2 HUMIDITY | MT | Humidity Transmitter(Integrated In TT) | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 40 | 60 | % | [19 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.4
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBA002 |  | TM140600TI039 | TM140600TT039 | TM140600TT039.MV | WAREHOUSE MCC ROOM 3 TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 0 | 50 | ˚C | [19 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.4
P-OKITM07-10-302-08-FLD-4641 | TM140600 | TM1406JBA002 |  | TM140600MI040 | TM140600MT040 | TM140600MT040.MV | WAREHOUSE MCC ROOM 3 HUMIDITY | MT | Humidity Transmitter(Integrated In TT) | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 40 | 60 | % | [19 empty] | 5 | HVAC VENDOR | Auto-Warehouse to TM14.4

## CVT Exchange Communication LST
PMT: |  |  |  |  | Design Institute: |  |  | Project No. | P-OKITM07-10 | [6 empty] | EXCHANGE COMMUNICTION LIST
[8 empty] | Project Name | DETAIL ENGINEERING FOR 4(FOUR) UNITS TISSUE MACHINE
[8 empty] | Doc. No. | P-OKITM07-10-500-06-LST-4405 | [7 empty] | Abbreviations
Owner: | [7 empty] | Rev. No. | 6 |  |  | Prep'd by | Dengzuijie |  |  |  | EER Electronic Equipment Room |  |  |  | SQRT Square Root
[8 empty] | Purpose | Final |  |  | Chk'd by | Chengjianguo |  |  |  | CCR Control Center Room
[8 empty] | Date | 30,8,2021 |  |  | Appv'd by | LiXiangdong |  |  |  | ESP Electrostatic Precipitator
P&ID No. | Area | Motor Tag reference | Loop No. | Tag No. | System Tag No. | Service Description | Signal Tag | Instrument Type | Location | System | IO Type | Signal |  |  | IO Loc. | PV LO | PV HI | Eng. Unit | Alarm | [6 empty] | State "0" | State "1" | CV Fail Action | CV Ctrl Action | PV CHAR | From |  | Cable |  |  | To |  | Rev. | Supply | Remarks
[12 empty] | Type | Power | Wire |  |  |  |  | LLL | LL | L | Nor. | H | HH | HHH | [5 empty] | JB/Panel No. | TB | Cable Number | Cable Type | Cable Order | Cabinet No. | TB |  | By
CONVERTING MILL BROKE
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM140517M001M1 | TM140517SC009 | TM140517SX009 | TM140517SX009.PRO | FINISHING PULPER AGITATOR SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | 5 |  | Converting Mill
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM140517U001M1 | TM140517SC012 | TM140517SX012 | TM140517SX012.PRO | BROKE CONVEYOR SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | 5 |  | Converting Mill
P-OKITM07-10-320-07-PID-3002 | TM140517 | TM140517C001M1 | TM140517SC018 | TM140517SX018 | TM140517SX018.PRO | FINISHING PULPER PUMP SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | 5 |  | Converting Mill
Motor IO List Except SC
P-OKITM07-10-320-07-PID-3002 | TM140517 |  | TM140517M001M1 | TM140517M001M1_CURR | DCS | FINISHING PULPER AGITATOR |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5 |  | Converting Mill
P-OKITM07-10-320-07-PID-3002 | TM140517 |  | TM140517M001M1 | TM140517M001M1_RF | DCS | FINISHING PULPER AGITATOR |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5 |  | Converting Mill
P-OKITM07-10-320-07-PID-3002 | TM140517 |  | TM140517M001M1 | TM140517M001M1_RY | DCS | FINISHING PULPER AGITATOR |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5 |  | Converting Mill
P-OKITM07-10-320-07-PID-3002 | TM140517 |  | TM140517M001M1 | TM140517M001M1_STR | DCS | FINISHING PULPER AGITATOR |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5 |  | Converting Mill
P-OKITM07-10-320-07-PID-3002 | TM140517 |  | TM140517U001M1 | TM140517U001M1_CURR | DCS | BROKE CONVEYOR |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5 |  | Converting Mill
P-OKITM07-10-320-07-PID-3002 | TM140517 |  | TM140517U001M1 | TM140517U001M1_RF | DCS | BROKE CONVEYOR |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5 |  | Converting Mill
P-OKITM07-10-320-07-PID-3002 | TM140517 |  | TM140517U001M1 | TM140517U001M1_RY | DCS | BROKE CONVEYOR |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5 |  | Converting Mill
P-OKITM07-10-320-07-PID-3002 | TM140517 |  | TM140517U001M1 | TM140517U001M1_STR | DCS | BROKE CONVEYOR |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5 |  | Converting Mill
P-OKITM07-10-320-07-PID-3002 | TM140517 |  | TM140517C001M1 | TM140517C001M1_CURR | DCS | FINISHING PULPER PUMP |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5 |  | Converting Mill
P-OKITM07-10-320-07-PID-3002 | TM140517 |  | TM140517C001M1 | TM140517C001M1_RF | DCS | FINISHING PULPER PUMP |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5 |  | Converting Mill
P-OKITM07-10-320-07-PID-3002 | TM140517 |  | TM140517C001M1 | TM140517C001M1_RY | DCS | FINISHING PULPER PUMP |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5 |  | Converting Mill
P-OKITM07-10-320-07-PID-3002 | TM140517 |  | TM140517C001M1 | TM140517C001M1_STR | DCS | FINISHING PULPER PUMP |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5 |  | Converting Mill

## IO Summary
I/O COUNT SUMMARY
| AI | AO | DI | DO | TOTAL | REMARK
SP2 DCS | 23 | 25 | 27 | 27 | 102
TM14.1 DCS | 5 |  | 6 |  | 11 | Auto-Warehouse HVAC
TM14.4 DCS | 8 | 0 | 11 | 0 | 19 | Auto-Warehouse HVAC
PRDS PLC | 4 | 2 | 0 | 0 | 6
SUM | 40 | 27 | 44 | 27 | 138

## Definitions
P&ID No. | The P&ID drawing number where the equipment is located.
Area | The Area where the equipment is located
Loop No. | Loop Number
Tag No. | Tag Name according to APP guideline
System Tag No. | Tag name to be appeared in DCS
Service Description | Process/service description
Signal Tag | Signal Tagname
Instrument Type | Type of instrument
Location | Location of the instrument
System | in DCS, PLC or local
IO Type | Type of input or output
Signal - Type | Signal type
Signal - Power | Power for the signal
Signal - Wire | wiring configuration
IO Loc. | Input and Output location
PV LO | Range Low
PV HI | Range High
Eng. Unit | Engineering Unit
Alarm | LLL- Low Low Low, HHH- High High High etc
State "0" | For Valves, If signal is zero, what willl be the valve opening.
State "1" | For Valves, If signal is one, what willl be the valve opening.
CV fail Action | For Valves, If air fails, what willl be the valve status.
CV Control Action | For Valves, Direction of the control.
PV CHAR | Process value characteristics
Rev | Revision
Supply By | Supplier name
Remarks