## SP2
PMT: | [5 empty] | Design Institute: |  |  | Project No. | P-OKITM07-10 | [6 empty] | DCS I/O Database
[9 empty] | Project Name | DETAIL ENGINEERING FOR 4(FOUR) UNITS TISSUE MACHINE
[9 empty] | Doc. No. | P-OKITM07-10-302-06-LST-4645 | [7 empty] | Abbreviations
Owner: | [8 empty] | Rev. No. | 7 |  |  | Prep'd by | Dengzuijie |  |  |  | EER Electronic Equipment Room |  |  |  | SQRT Square Root
[9 empty] | Purpose | Final |  |  | Chk'd by | Chengjianguo |  |  |  | CCR Control Center Room
[9 empty] | Date | 30,8,2021 |  |  | Appv'd by | LiXiangdong |  |  |  | ESP Electrostatic Precipitator
P&ID No. | Area | JB No. | ASD No. | Loop No. | Tag No. | System Tag No. | Service Description | Signal Tag | Instrument Type | Location | System | IO Type | Signal |  |  | IO Loc. | PV LO | PV HI | Eng. Unit | Alarm | [6 empty] | State "0" | State "1" | CV Fail Action | CV Ctrl Action | PV CHAR | From |  | Cable |  |  | To |  | Rev. | Supply | Remarks
[13 empty] | Type | Power | Wire |  |  |  |  | LLL | LL | L | Nor. | H | HH | HHH | [5 empty] | JB/Panel No. | TB | Cable Number | Cable Type | Cable Order | Cabinet No. | TB |  | By
LBKP Wet Line
P-OKITM07-10-302-07-PID-4641 | TM110012 |  |  | TM110012NC099 | TM110012NE099 |  | LBKP INTERMEDIATE TOWER PUMP 4 OUTPUT CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230VAC | [24 empty] | 2 |  |  | 1100 | 12 | NE |  | #N/A
P-OKITM07-10-302-07-PID-4641 | TM110012 | TM1100JBA005 |  | TM110012NC099 | TM110012NT099 | TM110012NT099.MV | LBKP INTERMEDIATE TOWER PUMP 4 OUTPUT CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 2 | 6 | %C | [19 empty] | 2 |  | located in SP1 area and connected to SP1 DCS | 1100 | 12 | NT | AI | %C
P-OKITM07-10-302-07-PID-4641 | TM110012 | TM1100JBD007 |  | TM110012NC099 | TM110012NS099 | TM110012NS099.MV | LBKP INTERMEDIATE TOWER PUMP 4 OUTPUT CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 2 |  | located in SP1 area and connected to SP1 DCS | 1100 | 12 | NS | DO | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012HS444 | TM140012SV444 | TM140012SV444 | LBKP INTERMEDIATE TOWER PUMP 4 OUTPUT To LBKP 2 INTERMEDIATE TOWER ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | 7 |  |  | 1400 | 12 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBS001 |  | TM140012HS444 | TM140012SV444.ZSC | TM140012SV444.GSC | LBKP INTERMEDIATE TOWER PUMP 4 OUTPUT To LBKP 2 INTERMEDIATE TOWER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 7 |  |  | 1400 | 12 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBS001 |  | TM140012HS444 | TM140012SV444.ZSO | TM140012SV444.GSO | LBKP INTERMEDIATE TOWER PUMP 4 OUTPUT To LBKP 2 INTERMEDIATE TOWER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 7 |  |  | 1400 | 12 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBS001 |  | TM140012HS444 | TM140012EV444 | TM140012EV444 | LBKP INTERMEDIATE TOWER PUMP 4 OUTPUT To LBKP 2 INTERMEDIATE TOWER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 7 |  |  | 1400 | 12 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012HS445 | TM140012SV445 | TM140012SV445 | LBKP INTERMEDIATE TOWER PUMP 4 OUTPUT To NBKP #3 DUMP TOWER ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | 7 |  |  | 1400 | 12 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBS001 |  | TM140012HS445 | TM140012SV445.ZSC | TM140012SV445.GSC | LBKP INTERMEDIATE TOWER PUMP 4 OUTPUT To NBKP #3 DUMP TOWER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 7 |  |  | 1400 | 12 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBS001 |  | TM140012HS445 | TM140012SV445.ZSO | TM140012SV445.GSO | LBKP INTERMEDIATE TOWER PUMP 4 OUTPUT To NBKP #3 DUMP TOWER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 7 |  |  | 1400 | 12 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBS001 |  | TM140012HS445 | TM140012EV445 | TM140012EV445 | LBKP INTERMEDIATE TOWER PUMP 4 OUTPUT To NBKP #3 DUMP TOWER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 7 |  |  | 1400 | 12 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBA001 |  | TM140012LI450 | TM140012LT450 | TM140012LT450.MV | LBKP 2 INTERMEDIATE TOWER LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 9000 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1 |  |  | 1400 | 12 | LT | AI | %,mm
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012HS451 | TM140012SV451 | TM140012SV451 | LBKP 2 INTERMEDIATE TOWER PUMP 1 INLET ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 12 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBS001 |  | TM140012HS451 | TM140012SV451.ZSC | TM140012SV451.GSC | LBKP 2 INTERMEDIATE TOWER PUMP 1 INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 12 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBS001 |  | TM140012HS451 | TM140012SV451.ZSO | TM140012SV451.GSO | LBKP 2 INTERMEDIATE TOWER PUMP 1 INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 12 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBS001 |  | TM140012HS451 | TM140012EV451 | TM140012EV451 | LBKP 2 INTERMEDIATE TOWER PUMP 1 INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 12 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012NC452 | TM140012NE452 |  | LBKP 2 INTERMEDIATE TOWER PUMP 1 OUTPUT CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230VAC | [24 empty] | B |  |  | 1400 | 12 | NE |  | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBA001 |  | TM140012NC452 | TM140012NT452 | TM140012NT452.MV | LBKP 2 INTERMEDIATE TOWER PUMP 1 OUTPUT CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 2 | 6 | %C | [19 empty] | 1 |  |  | 1400 | 12 | NT | AI | %C
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBD001 |  | TM140012NC452 | TM140012NS452 | TM140012NS452.MV | LBKP 2 INTERMEDIATE TOWER PUMP 1 OUTPUT CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  |  | 1400 | 12 | NS | DO | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBA001 | TM1400ASD001 | TM140012NC452 | TM140012NV452 | TM140012NV452.OUT | LBKP 2 INTERMEDIATE TOWER PUMP 1 OUTPUT CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 12 | NV | AO | %
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBA001 |  | TM140012PC453 | TM140012PT453 | TM140012PT453.MV | LBKP 2 INTERMEDIATE TOWER PUMP 1 OUTPUT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  |  | 1400 | 12 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012HS461 | TM140012SV461 | TM140012SV461 | LBKP 2 INTERMEDIATE TOWER PUMP 2 INLET ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 12 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBS001 |  | TM140012HS461 | TM140012SV461.ZSC | TM140012SV461.GSC | LBKP 2 INTERMEDIATE TOWER PUMP 2 INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 12 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBS001 |  | TM140012HS461 | TM140012SV461.ZSO | TM140012SV461.GSO | LBKP 2 INTERMEDIATE TOWER PUMP 2 INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 12 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBS001 |  | TM140012HS461 | TM140012EV461 | TM140012EV461 | LBKP 2 INTERMEDIATE TOWER PUMP 2 INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 12 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012NC462 | TM140012NE462 |  | LBKP 2 INTERMEDIATE TOWER PUMP 2 OUTPUT CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230VAC | [24 empty] | B |  |  | 1400 | 12 | NE |  | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBA001 |  | TM140012NC462 | TM140012NT462 | TM140012NT462.MV | LBKP 2 INTERMEDIATE TOWER PUMP 2 OUTPUT CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 2 | 6 | %C | [19 empty] | 1 |  |  | 1400 | 12 | NT | AI | %C
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBD001 |  | TM140012NC462 | TM140012NS462 | TM140012NS462.MV | LBKP 2 INTERMEDIATE TOWER PUMP 2 OUTPUT CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  |  | 1400 | 12 | NS | DO | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBA001 | TM1400ASD001 | TM140012NC462 | TM140012NV462 | TM140012NV462.OUT | LBKP 2 INTERMEDIATE TOWER PUMP 2 OUTPUT CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 12 | NV | AO | %
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBA001 |  | TM140012PC463 | TM140012PT463 | TM140012PT463.MV | LBKP 2 INTERMEDIATE TOWER PUMP 2 OUTPUT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  |  | 1400 | 12 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012HS471 | TM140012SV471 | TM140012SV471 | LBKP 2 INTERMEDIATE TOWER PUMP 3 INLET ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 12 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBS001 |  | TM140012HS471 | TM140012SV471.ZSC | TM140012SV471.GSC | LBKP 2 INTERMEDIATE TOWER PUMP 3 INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 12 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBS001 |  | TM140012HS471 | TM140012SV471.ZSO | TM140012SV471.GSO | LBKP 2 INTERMEDIATE TOWER PUMP 3 INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 12 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBS001 |  | TM140012HS471 | TM140012EV471 | TM140012EV471 | LBKP 2 INTERMEDIATE TOWER PUMP 3 INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 12 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012NC472 | TM140012NE472 |  | LBKP 2 INTERMEDIATE TOWER PUMP 3 OUTPUT CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230VAC | [24 empty] | B |  |  | 1400 | 12 | NE |  | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBA001 |  | TM140012NC472 | TM140012NT472 | TM140012NT472.MV | LBKP 2 INTERMEDIATE TOWER PUMP 3 OUTPUT CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 2 | 6 | %C | [19 empty] | 1 |  |  | 1400 | 12 | NT | AI | %C
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBD001 |  | TM140012NC472 | TM140012NS472 | TM140012NS472.MV | LBKP 2 INTERMEDIATE TOWER PUMP 3 OUTPUT CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  |  | 1400 | 12 | NS | DO | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBA001 | TM1400ASD001 | TM140012NC472 | TM140012NV472 | TM140012NV472.OUT | LBKP 2 INTERMEDIATE TOWER PUMP 3 OUTPUT CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 12 | NV | AO | %
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBA001 |  | TM140012PC473 | TM140012PT473 | TM140012PT473.MV | LBKP 2 INTERMEDIATE TOWER PUMP 3 OUTPUT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  |  | 1400 | 12 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012HS481 | TM140012SV481 | TM140012SV481 | LBKP 2 INTERMEDIATE TOWER PUMP 4 INLET ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 12 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBS001 |  | TM140012HS481 | TM140012SV481.ZSC | TM140012SV481.GSC | LBKP 2 INTERMEDIATE TOWER PUMP 4 INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 12 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBS001 |  | TM140012HS481 | TM140012SV481.ZSO | TM140012SV481.GSO | LBKP 2 INTERMEDIATE TOWER PUMP 4 INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 12 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBS001 |  | TM140012HS481 | TM140012EV481 | TM140012EV481 | LBKP 2 INTERMEDIATE TOWER PUMP 4 INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 12 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012NC482 | TM140012NE482 |  | LBKP 2 INTERMEDIATE TOWER PUMP 4 OUTPUT CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230VAC | [24 empty] | B |  |  | 1400 | 12 | NE |  | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBA001 |  | TM140012NC482 | TM140012NT482 | TM140012NT482.MV | LBKP 2 INTERMEDIATE TOWER PUMP 4 OUTPUT CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 2 | 6 | %C | [19 empty] | 1 |  |  | 1400 | 12 | NT | AI | %C
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBD001 |  | TM140012NC482 | TM140012NS482 | TM140012NS482.MV | LBKP 2 INTERMEDIATE TOWER PUMP 4 OUTPUT CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  |  | 1400 | 12 | NS | DO | #N/A
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBA001 | TM1400ASD001 | TM140012NC482 | TM140012NV482 | TM140012NV482.OUT | LBKP 2 INTERMEDIATE TOWER PUMP 4 OUTPUT CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 12 | NV | AO | %
P-OKITM07-10-302-07-PID-4641 | TM140012 | TM1400JBA001 |  | TM140012PC483 | TM140012PT483 | TM140012PT483.MV | LBKP 2 INTERMEDIATE TOWER PUMP 4 OUTPUT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  |  | 1400 | 12 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
| Broke Line | [43 empty] | #N/A | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBA002 |  | TM140017LI450 | TM140017LT450 | TM140017LT450.MV | BROKE TOWER LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10500 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1 |  |  | 1400 | 17 | LT | AI | %,mm
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017HS451 | TM140017SV451 | TM140017SV451 | BROKE TOWER PUMP 1 INLET ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 17 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBS005 |  | TM140017HS451 | TM140017SV451.ZSC | TM140017SV451.GSC | BROKE TOWER PUMP 1 INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 17 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBS005 |  | TM140017HS451 | TM140017SV451.ZSO | TM140017SV451.GSO | BROKE TOWER PUMP 1 INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 17 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBS005 |  | TM140017HS451 | TM140017EV451 | TM140017EV451 | BROKE TOWER PUMP 1 INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 17 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017NC452 | TM140017NE452 |  | BROKE TOWER PUMP 1 OUTPUT CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230VAC | [24 empty] | B |  |  | 1400 | 17 | NE |  | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBA002 |  | TM140017NC452 | TM140017NT452 | TM140017NT452.MV | BROKE TOWER PUMP 1 OUTPUT CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 2 | 6 | %C | [19 empty] | 1 |  |  | 1400 | 17 | NT | AI | %C
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBD002 |  | TM140017NC452 | TM140017NS452 | TM140017NS452.MV | BROKE TOWER PUMP 1 OUTPUT CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  |  | 1400 | 17 | NS | DO | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBA002 | TM1400ASD003 | TM140017NC452 | TM140017NV452 | TM140017NV452.OUT | BROKE TOWER PUMP 1 OUTPUT CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 17 | NV | AO | %
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBA002 |  | TM140017PC453 | TM140017PT453 | TM140017PT453.MV | BROKE TOWER PUMP 1 OUTPUT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  |  | 1400 | 17 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017HS461 | TM140017SV461 | TM140017SV461 | BROKE TOWER PUMP 2 INLET ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 17 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBS005 |  | TM140017HS461 | TM140017SV461.ZSC | TM140017SV461.GSC | BROKE TOWER PUMP 2 INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 17 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBS005 |  | TM140017HS461 | TM140017SV461.ZSO | TM140017SV461.GSO | BROKE TOWER PUMP 2 INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 17 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBS005 |  | TM140017HS461 | TM140017EV461 | TM140017EV461 | BROKE TOWER PUMP 2 INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 17 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017NC462 | TM140017NE462 |  | BROKE TOWER PUMP 2 OUTPUT CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230VAC | [24 empty] | B |  |  | 1400 | 17 | NE |  | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBA002 |  | TM140017NC462 | TM140017NT462 | TM140017NT462.MV | BROKE TOWER PUMP 2 OUTPUT CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 2 | 6 | %C | [19 empty] | 1 |  |  | 1400 | 17 | NT | AI | %C
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBD002 |  | TM140017NC462 | TM140017NS462 | TM140017NS462.MV | BROKE TOWER PUMP 2 OUTPUT CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  |  | 1400 | 17 | NS | DO | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBA002 | TM1400ASD003 | TM140017NC462 | TM140017NV462 | TM140017NV462.OUT | BROKE TOWER PUMP 2 OUTPUT CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 17 | NV | AO | %
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBA002 |  | TM140017PC463 | TM140017PT463 | TM140017PT463.MV | BROKE TOWER PUMP 2 OUTPUT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  |  | 1400 | 17 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017HS471 | TM140017SV471 | TM140017SV471 | BROKE TOWER PUMP 3 INLET ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 17 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBS005 |  | TM140017HS471 | TM140017SV471.ZSC | TM140017SV471.GSC | BROKE TOWER PUMP 3 INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 17 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBS005 |  | TM140017HS471 | TM140017SV471.ZSO | TM140017SV471.GSO | BROKE TOWER PUMP 3 INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 17 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBS005 |  | TM140017HS471 | TM140017EV471 | TM140017EV471 | BROKE TOWER PUMP 3 INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 17 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017NC472 | TM140017NE472 |  | BROKE TOWER PUMP 3 OUTPUT CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230VAC | [24 empty] | B |  |  | 1400 | 17 | NE |  | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBA002 |  | TM140017NC472 | TM140017NT472 | TM140017NT472.MV | BROKE TOWER PUMP 3 OUTPUT CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 2 | 6 | %C | [19 empty] | 1 |  |  | 1400 | 17 | NT | AI | %C
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBD002 |  | TM140017NC472 | TM140017NS472 | TM140017NS472.MV | BROKE TOWER PUMP 3 OUTPUT CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  |  | 1400 | 17 | NS | DO | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBA002 | TM1400ASD003 | TM140017NC472 | TM140017NV472 | TM140017NV472.OUT | BROKE TOWER PUMP 3 OUTPUT CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 17 | NV | AO | %
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBA002 |  | TM140017PC473 | TM140017PT473 | TM140017PT473.MV | BROKE TOWER PUMP 3 OUTPUT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  |  | 1400 | 17 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017HS481 | TM140017SV481 | TM140017SV481 | BROKE TOWER PUMP 4 INLET ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 17 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBS005 |  | TM140017HS481 | TM140017SV481.ZSC | TM140017SV481.GSC | BROKE TOWER PUMP 4 INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 17 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBS005 |  | TM140017HS481 | TM140017SV481.ZSO | TM140017SV481.GSO | BROKE TOWER PUMP 4 INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 17 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBS005 |  | TM140017HS481 | TM140017EV481 | TM140017EV481 | BROKE TOWER PUMP 4 INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 17 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017NC482 | TM140017NE482 |  | BROKE TOWER PUMP 4 OUTPUT CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230VAC | [24 empty] | B |  |  | 1400 | 17 | NE |  | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBA002 |  | TM140017NC482 | TM140017NT482 | TM140017NT482.MV | BROKE TOWER PUMP 4 OUTPUT CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 2 | 6 | %C | [19 empty] | 1 |  |  | 1400 | 17 | NT | AI | %C
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBD002 |  | TM140017NC482 | TM140017NS482 | TM140017NS482.MV | BROKE TOWER PUMP 4 OUTPUT CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  |  | 1400 | 17 | NS | DO | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBA002 | TM1400ASD003 | TM140017NC482 | TM140017NV482 | TM140017NV482.OUT | BROKE TOWER PUMP 4 OUTPUT CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 17 | NV | AO | %
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBA002 |  | TM140017PC483 | TM140017PT483 | TM140017PT483.MV | BROKE TOWER PUMP 4 OUTPUT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  |  | 1400 | 17 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017HS491 | TM140017SV491 | TM140017SV491 | BROKE TOWER PUMP 5 INLET ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 17 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBS005 |  | TM140017HS491 | TM140017SV491.ZSC | TM140017SV491.GSC | BROKE TOWER PUMP 5 INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 17 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBS005 |  | TM140017HS491 | TM140017SV491.ZSO | TM140017SV491.GSO | BROKE TOWER PUMP 5 INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 17 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4642 | TM140017 | TM1400JBS005 |  | TM140017HS491 | TM140017EV491 | TM140017EV491 | BROKE TOWER PUMP 5 INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 17 | EV | DO | #N/A
| NBKP 3# Line | [43 empty] | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS201 | TM140011SV201 | TM140011SV201 | NBKP #1 REFINED TOWER PUMP 4 INLET ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS010 |  | TM140011HS201 | TM140011SV201.ZSC | TM140011SV201.GSC | NBKP #1 REFINED TOWER PUMP 4 INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS010 |  | TM140011HS201 | TM140011SV201.ZSO | TM140011SV201.GSO | NBKP #1 REFINED TOWER PUMP 4 INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS010 |  | TM140011HS201 | TM140011EV201 | TM140011EV201 | NBKP #1 REFINED TOWER PUMP 4 INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NC202 | TM140011NE202 |  | NBKP #1 REFINED TOWER PUMP 4 OUTPUT CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230VAC | [24 empty] | B |  |  | 1400 | 11 | NE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA004 |  | TM140011NC202 | TM140011NT202 | TM140011NT202.MV | NBKP #1 REFINED TOWER PUMP 4 OUTPUT CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 2 | 6 | %C | [19 empty] | 1 |  |  | 1400 | 11 | NT | AI | %C
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD005 |  | TM140011NC202 | TM140011NS202 | TM140011NS202.MV | NBKP #1 REFINED TOWER PUMP 4 OUTPUT CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  |  | 1400 | 11 | NS | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA004 | TM1400ASD005 | TM140011NC202 | TM140011NV202 | TM140011NV202.OUT | NBKP #1 REFINED TOWER PUMP 4 OUTPUT CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 11 | NV | AO | %
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA004 |  | TM140011PC203 | TM140011PT203 | TM140011PT203.MV | NBKP #1 REFINED TOWER PUMP 4 OUTPUT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  |  | 1400 | 11 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS211 | TM140011SV211 | TM140011SV211 | NBKP #2 REFINED TOWER PUMP 4 INLET ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS010 |  | TM140011HS211 | TM140011SV211.ZSC | TM140011SV211.GSC | NBKP #2 REFINED TOWER PUMP 4 INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS010 |  | TM140011HS211 | TM140011SV211.ZSO | TM140011SV211.GSO | NBKP #2 REFINED TOWER PUMP 4 INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS010 |  | TM140011HS211 | TM140011EV211 | TM140011EV211 | NBKP #2 REFINED TOWER PUMP 4 INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NC212 | TM140011NE212 |  | NBKP #2 REFINED TOWER PUMP 4 OUTPUT CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230VAC | [24 empty] | B |  |  | 1400 | 11 | NE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA004 |  | TM140011NC212 | TM140011NT212 | TM140011NT212.MV | NBKP #2 REFINED TOWER PUMP 4 OUTPUT CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 2 | 6 | %C | [19 empty] | 1 |  |  | 1400 | 11 | NT | AI | %C
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD005 |  | TM140011NC212 | TM140011NS212 | TM140011NS212.MV | NBKP #2 REFINED TOWER PUMP 4 OUTPUT CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  |  | 1400 | 11 | NS | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA004 | TM1400ASD005 | TM140011NC212 | TM140011NV212 | TM140011NV212.OUT | NBKP #2 REFINED TOWER PUMP 4 OUTPUT CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 11 | NV | AO | %
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA004 |  | TM140011PC213 | TM140011PT213 | TM140011PT213.MV | NBKP #2 REFINED TOWER PUMP 4 OUTPUT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  |  | 1400 | 11 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011FFC002 | TM140011FE002 |  | WHITE WATER TO NBKP #3 PULPER FLOW | FE | Magnetic Flow Sensor | Field | [31 empty] | 1400 | 11 | FE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 |  | TM140011FFC002 | TM140011FT002 | TM140011FT002.MV | WHITE WATER TO NBKP #3 PULPER FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 0 | 13000 | l/min | [19 empty] | 1 |  |  | 1400 | 11 | FT | AI | l/min,kg/h,mc/h,t / hr,m3/hr
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 | TM1400ASD004 | TM140011FFC002 | TM140011FV002A | TM140011FV002A.OUT | WHITE WATER TO NBKP #3 PULPER FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 11 | FV | AO | %
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 | TM1400ASD004 | TM140011FFC002 | TM140011FV002B | TM140011FV002B.OUT | WHITE WATER TO NBKP #3 PULPER OUTLET FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 11 | FV | AO | %
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD003 |  | TM140011FS003 | TM140011FS003 | TM140011FS003.L | SEALING WATER TO NBKP #3 PULPER FLOW L | FS | Flow Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0.5 | 3 | l/min | [7 empty] | Flow L | Not Flow L | [10 empty] | 1 | Andritz |  | 1400 | 11 | FS | DI | l/min
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS004 | TM140011SV004 | TM140011SV004 | SEALING WATER TO NBKP #3 PULPER ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS006 |  | TM140011HS004 | TM140011SV004.ZSC | TM140011SV004.GSC | SEALING WATER TO NBKP #3 PULPER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS006 |  | TM140011HS004 | TM140011SV004.ZSO | TM140011SV004.GSO | SEALING WATER TO NBKP #3 PULPER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS006 |  | TM140011HS004 | TM140011EV004 | TM140011EV004 | SEALING WATER TO NBKP #3 PULPER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS006 | TM140011SV006 | TM140011SV006 | PULP FROM NBKP #3 PULPER ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS006 |  | TM140011HS006 | TM140011SV006.ZSC | TM140011SV006.GSC | PULP FROM NBKP #3 PULPER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS006 |  | TM140011HS006 | TM140011SV006.ZSO | TM140011SV006.GSO | PULP FROM NBKP #3 PULPER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS006 |  | TM140011HS006 | TM140011EV006 | TM140011EV006 | PULP FROM NBKP #3 PULPER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 |  | TM140011LI007 | TM140011LT007 | TM140011LT007.MV | NBKP #3 PULPER LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 2200 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1 |  |  | 1400 | 11 | LT | AI | %,mm
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS008 | TM140011SV008 | TM140011SV008 | NBKP #3 PULP TO NBKP #3 DUMP TOWER ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS006 |  | TM140011HS008 | TM140011SV008.ZSC | TM140011SV008.GSC | NBKP #3 PULP TO NBKP #3 DUMP TOWER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS006 |  | TM140011HS008 | TM140011SV008.ZSO | TM140011SV008.GSO | NBKP #3 PULP TO NBKP #3 DUMP TOWER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS006 |  | TM140011HS008 | TM140011EV008 | TM140011EV008 | NBKP #3 PULP TO NBKP #3 DUMP TOWER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA002 |  | TM140011LI009 | TM140011LT009 | TM140011LT009.MV | NBKP #3 DUMP TOWER LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 9000 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1 |  |  | 1400 | 11 | LT | AI | %,mm
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS010 | TM140011SV010 | TM140011SV010 | NBKP #3 DUMP TOWER OUTLET ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS010 | TM140011SV010.ZSC | TM140011SV010.GSC | NBKP #3 DUMP TOWER OUTLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS010 | TM140011SV010.ZSO | TM140011SV010.GSO | NBKP #3 DUMP TOWER OUTLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS010 | TM140011EV010 | TM140011EV010 | NBKP #3 DUMP TOWER OUTLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NC011 | TM140011NE011 |  | NBKP #3 DUMP TOWER PUMP OUTLET CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230VAC | [24 empty] | B |  |  | 1400 | 11 | NE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA002 |  | TM140011NC011 | TM140011NT011 | TM140011NT011.MV | NBKP #3 DUMP TOWER PUMP OUTLET CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 0 | 6 | %C | [19 empty] | 1 |  |  | 1400 | 11 | NT | AI | %C
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD002 |  | TM140011NC011 | TM140011NS011 | TM140011NS011.MV | NBKP #3 DUMP TOWER PUMP OUTLET CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  |  | 1400 | 11 | NS | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA002 | TM1400ASD002 | TM140011NC011 | TM140011NV011 | TM140011NV011.OUT | NBKP #3 DUMP TOWER PUMP OUTLET CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 11 | NV | AO | %
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011AC013 | TM140011AE013 |  | NBKP #3 PULPER PUMP OUTLET PH | AE | pH Sensor | Field | DCS | [30 empty] | 1400 | 11 | AE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 |  | TM140011AC013 | TM140011AT013 | TM140011AT013.MV | NBKP #3 PULPER PUMP OUTLET PH | AT | pH Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 14 | Ph | [19 empty] | 3 |  |  | 1400 | 11 | AT | AI | Ph,ml CSF
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011KS014 | TM140011KX014 | TM140011KX014.SOF | NBKP #3 HD-CLEANER JUNK TRAP SEQUENCE | KX | DCS software function | DCS | DCS |  | Software function | [28 empty] | 1400 | 11 | KX |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS014A | TM140011SV014A | TM140011SV014A | NBKP #3 HD-CLEANER JUNK TRAP TOP ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B | Andritz |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD006 |  | TM140011HS014A | TM140011SV014A.ZSC | TM140011SV014A.GSC | NBKP #3 HD-CLEANER JUNK TRAP TOP ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 | Andritz |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD006 |  | TM140011HS014A | TM140011SV014A.ZSO | TM140011SV014A.GSO | NBKP #3 HD-CLEANER JUNK TRAP TOP ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 | Andritz |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD006 | TM1400ASD008 | TM140011HS014A | TM140011EV014A | TM140011EV014A | NBKP #3 HD-CLEANER JUNK TRAP TOP ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 | Andritz |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS014B | TM140011SV014B | TM140011SV014B | NBKP #3 HD-CLEANER JUNK TRAP BOTTOM ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B | Andritz |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD006 |  | TM140011HS014B | TM140011SV014B.ZSC | TM140011SV014B.GSC | NBKP #3 HD-CLEANER JUNK TRAP BOTTOM ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 | Andritz |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD006 |  | TM140011HS014B | TM140011SV014B.ZSO | TM140011SV014B.GSO | NBKP #3 HD-CLEANER JUNK TRAP BOTTOM ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 | Andritz |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD006 | TM1400ASD008 | TM140011HS014B | TM140011EV014B | TM140011EV014B | NBKP #3 HD-CLEANER JUNK TRAP BOTTOM ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 | Andritz |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS014C | TM140011SV014C | TM140011SV014C | NBKP #3 HD-CLEANER JUNK TRAP TOP FLUSHING ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B | Andritz |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD006 |  | TM140011HS014C | TM140011SV014C.ZSC | TM140011SV014C.GSC | NBKP #3 HD-CLEANER JUNK TRAP TOP FLUSHING ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 | Andritz |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD006 |  | TM140011HS014C | TM140011SV014C.ZSO | TM140011SV014C.GSO | NBKP #3 HD-CLEANER JUNK TRAP TOP FLUSHING ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 | Andritz |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD006 | TM1400ASD008 | TM140011HS014C | TM140011EV014C | TM140011EV014C | NBKP #3 HD-CLEANER JUNK TRAP TOP FLUSHING ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 | Andritz |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS014D | TM140011SV014D | TM140011SV014D | NBKP #3 HD-CLEANER JUNK TRAP BOTTOM FLUSHING ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B | Andritz |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD006 |  | TM140011HS014D | TM140011SV014D.ZSC | TM140011SV014D.GSC | NBKP #3 HD-CLEANER JUNK TRAP BOTTOM FLUSHING ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 | Andritz |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD006 |  | TM140011HS014D | TM140011SV014D.ZSO | TM140011SV014D.GSO | NBKP #3 HD-CLEANER JUNK TRAP BOTTOM FLUSHING ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 | Andritz |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD006 | TM1400ASD008 | TM140011HS014D | TM140011EV014D | TM140011EV014D | NBKP #3 HD-CLEANER JUNK TRAP BOTTOM FLUSHING ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 | Andritz |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS014E | TM140011SV014E | TM140011SV014E | NBKP #3 HD-CLEANER JUNK TRAP EXHAUSTING ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B | Andritz |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD006 |  | TM140011HS014E | TM140011SV014E.ZSC | TM140011SV014E.GSC | NBKP #3 HD-CLEANER JUNK TRAP EXHAUSTING ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 | Andritz |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD006 |  | TM140011HS014E | TM140011SV014E.ZSO | TM140011SV014E.GSO | NBKP #3 HD-CLEANER JUNK TRAP EXHAUSTING ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 | Andritz |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD006 | TM1400ASD008 | TM140011HS014E | TM140011EV014E | TM140011EV014E | NBKP #3 HD-CLEANER JUNK TRAP EXHAUSTING ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 | Andritz |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 |  | TM140011PC015 | TM140011PT015 | TM140011PT015.MV | NBKP #3 HD-CLEANER FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 5 | Bar.g | [19 empty] | 1 |  |  | 1400 | 11 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 |  | TM140011PC016 | TM140011PT016 | TM140011PT016.MV | NBKP #3 HD-CLEANER ACCEPT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 5 | Bar.g | [19 empty] | 1 |  |  | 1400 | 11 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 | TM1400ASD004 | TM140011PC016 | TM140011PV016 | TM140011PV016.OUT | NBKP #3 HD-CLEANER ACCEPT PRESSURE CV SETPOINT | PV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 11 | PV | AO | %,bar
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS017 | TM140011SV017 | TM140011SV017 | NBKP #3 HD-CLEANER FEED ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B |  |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS017 | TM140011SV017.ZSC | TM140011SV017.GSC | NBKP #3 HD-CLEANER FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS017 | TM140011SV017.ZSO | TM140011SV017.GSO | NBKP #3 HD-CLEANER FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS017 | TM140011EV017 | TM140011EV017 | NBKP #3 HD-CLEANER FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS018 | TM140011SV018 | TM140011SV018 | NBKP #3 HD-CLEANER ACCEPT ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B |  |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS018 | TM140011SV018.ZSC | TM140011SV018.GSC | NBKP #3 HD-CLEANER ACCEPT ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS018 | TM140011SV018.ZSO | TM140011SV018.GSO | NBKP #3 HD-CLEANER ACCEPT ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS018 | TM140011EV018 | TM140011EV018 | NBKP #3 HD-CLEANER ACCEPT ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS019 | TM140011SV019 | TM140011SV019 | NBKP #3 HD-CLEANER BYPASS ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B |  |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS019 | TM140011SV019.ZSC | TM140011SV019.GSC | NBKP #3 HD-CLEANER BYPASS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS019 | TM140011SV019.ZSO | TM140011SV019.GSO | NBKP #3 HD-CLEANER BYPASS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS019 | TM140011EV019 | TM140011EV019 | NBKP #3 HD-CLEANER BYPASS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011TC020 | TM140011TE020 |  | NBKP #3 PULPERTEMPERATURE | TE | Temperature Sensor | Field | [28 empty] | B |  |  | 1400 | 11 | TE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 |  | TM140011TC020 | TM140011TT020 | TM140011TT020.MV | NBKP #3 PULPERTEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [19 empty] | 1 |  |  | 1400 | 11 | TT | AI | °C,℃,˚C
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 | TM1400ASD004 | TM140011TC020 | TM140011TV020 | TM140011TV020.OUT | NBKP #3 PULPERTEMPERATURE CV SETPOINT | TV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [9 empty] | Close | [9 empty] | 1 |  |  | 1400 | 11 | TV | AO | %
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011FC021 | TM140011FE021 |  | NaOH Tank 2 Pump 1/2 TO NBKP #3 PULPER FLOW | FE | Magnetic Flow Sensor | Field | [31 empty] | 1400 | 11 | FE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 |  | TM140011FC021 | TM140011FT021 | TM140011FT021.MV | NaOH Tank 2 Pump 1/2 TO NBKP #3 PULPER FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 0 | 30 | l/min | [19 empty] | 1 |  |  | 1400 | 11 | FT | AI | l/min,kg/h,mc/h,t / hr,m3/hr
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 | TM1400ASD004 | TM140011FC021 | TM140011FV021 | TM140011FV021.OUT | NaOH Tank 2 Pump 1/2 TO NBKP #3 PULPER FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 11 | FV | AO | %
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 |  | TM140011FI022 | TM140011FT022 | TM140011FT022.MV | SP MAIN STAEM FLOW | FT | Vortex flow transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 4 | t / hr | [19 empty] | 1 |  |  | 1400 | 11 | FT | AI | l/min,kg/h,mc/h,t / hr,m3/hr
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 |  | TM140011PI023 | TM140011PT023 | TM140011PT023.MV | SP MAIN STAEM PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 15 | Bar.g | [19 empty] | 1 |  |  | 1400 | 11 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011TI024 | TM140011TE024 |  | SP MAIN STAEM TEMPERATURE | TE | Temperature sensor | Field | [31 empty] | 1400 | 11 | TE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 |  | TM140011TI024 | TM140011TT024 | TM140011TT024.MV | SP MAIN STAEM TEMPERATURE | TT | Temperature transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 230 | ˚C | [19 empty] | 1 |  |  | 1400 | 11 | TT | AI | °C,℃,˚C
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS025 | TM140011SV025 | TM140011SV025 | NBKP #3 PULPER PUMP RECIRCULATION ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS006 |  | TM140011HS025 | TM140011SV025.ZSC | TM140011SV025.GSC | NBKP #3 PULPER PUMP RECIRCULATION ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS006 |  | TM140011HS025 | TM140011SV025.ZSO | TM140011SV025.GSO | NBKP #3 PULPER PUMP RECIRCULATION ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS006 |  | TM140011HS025 | TM140011EV025 | TM140011EV025 | NBKP #3 PULPER PUMP RECIRCULATION ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS026 | TM140011SV026 | TM140011SV026 | NBKP #3 PULPER REJECT ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS006 |  | TM140011HS026 | TM140011SV026.ZSC | TM140011SV026.GSC | NBKP #3 PULPER REJECT ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 3 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS006 |  | TM140011HS026 | TM140011SV026.ZSO | TM140011SV026.GSO | NBKP #3 PULPER REJECT ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 3 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS006 |  | TM140011HS026 | TM140011EV026 | TM140011EV026 | NBKP #3 PULPER REJECT ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 3 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS027 | TM140011SV027 | TM140011SV027 | NBKP #3 PULPER REJECT PIPE FLUSHING WATER ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS006 |  | TM140011HS027 | TM140011SV027.ZSC | TM140011SV027.GSC | NBKP #3 PULPER REJECT PIPE FLUSHING WATER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 3 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS006 |  | TM140011HS027 | TM140011SV027.ZSO | TM140011SV027.GSO | NBKP #3 PULPER REJECT PIPE FLUSHING WATER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 3 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS006 |  | TM140011HS027 | TM140011EV027 | TM140011EV027 | NBKP #3 PULPER REJECT PIPE FLUSHING WATER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 3 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD003 |  | TM140011SS044 | TM140011SS044 | TM140011SS044 | FEEDING CONVEYOR SPEED | SS | Speed Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 | Andritz |  | 1400 | 11 | SS | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD003 |  | TM140011GS045 | TM140011GS045.A | TM140011GS045.A | CHAIN CONVEYOR POSITION | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC EXTERNAL | 2 | RR | [10 empty] | Front Position | Not Front Position | [10 empty] | 1 | Andritz |  | 1400 | 11 | A | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD003 |  | TM140011GS045 | TM140011GS045.B | TM140011GS045.B | FEEDING CONVEYOR POSITION | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC EXTERNAL | 2 | RR | [10 empty] | Back Position | Not Back Position | [10 empty] | 1 | Andritz |  | 1400 | 11 | B | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011XS047 | TM140011CP01 | TM1400111CC01 | BALE RECIEVING CONVEYOR LOCAL CONTROL PANEL | [31 empty] | B | Andritz |  | 1400 | 11 | CP | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CP01 |  | TM140011XS047 | TM140011FC P01. 047 | TM140011FC P01. 047.MANL | MAUNAL RUN LAMP/RUN LAMP | FC P01 | Indicator light | +CC01 | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | Andritz | +CC01 | 1400 P01. 047 | 11 P01. 047 | FC P01. 047 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CP01 |  | TM140011XS047 | TM140011FC P02. 047 | TM140011FC P02. 047.AUTL | AUTO RUN LAMP/METAL ALARM LAMP | FC P02 | Indicator light | +CC01 | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | Andritz | +CC01 | 1400 P02. 047 | 11 P02. 047 | FC P02. 047 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CP01 |  | TM140011XS047 | TM140011FC S01. 047 | TM140011FC S01. 047.MANC | MAUNAL RUN/FEED CONFIRM | FC S01 | Push Button | +CC01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | Andritz | +CC01 | 1400 S01. 047 | 11 S01. 047 | FC S01. 047 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CP01 |  | TM140011XS047 | TM140011FC S02. 047 | TM140011FC S02. 047.AUTC | AUTO RUN/METAL ALARM OK | FC S02 | Push Button | +CC01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | Andritz | +CC01 | 1400 S02. 047 | 11 S02. 047 | FC S02. 047 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CP01 |  | TM140011XS047 | TM140011FC S03. 047 | TM140011FC S03. 047.SPA | SPARE | FC S03 | Push Button | +CC01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | Andritz | +CC01 | 1400 S03. 047 | 11 S03. 047 | FC S03. 047 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CP01 |  | TM140011XS047 | TM140011FC S05. 047 | TM140011FC S05. 047.L/R | LOCAL/DCS | FC S05 | Select Switch | +CC01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | Andritz | +CC01 | 1400 S05. 047 | 11 S05. 047 | FC S05. 047 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CP01 |  | TM140011XS047 | TM140011.101S1.047 | TM140011.101S1.047.FWD | BALE RECIEVING CONVEYOR 1 LOCAL START FWD | 101 S1 | Push Button | +CC01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | Andritz | +CC01 | 1400101S1.047 | 11101S1.047 | 101S1.047 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CP01 |  | TM140011XS047 | TM140011.101S2.047 | TM140011.101S2.047.REV | BALE RECIEVING CONVEYOR 1 LOCAL START REV | 101 S2 | Push Button | +CC01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | Andritz | +CC01 | 1400101S2.047 | 11101S2.047 | 101S2.047 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CP01 |  | TM140011XS047 | TM140011.103S1.047 | TM140011.103S1.047.FWD | BALE CONVEYOR LOCAL START FWD | 103 S1 | Push Button | +CC01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | Andritz | +CC01 | 1400103S1.047 | 11103S1.047 | 103S1.047 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CP01 |  | TM140011XS047 | TM140011.103S2.047 | TM140011.103S2.047.REV | BALE CONVEYOR LOCAL START REV | 103 S2 | Push Button | +CC01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | Andritz | +CC01 | 1400103S2.047 | 11103S2.047 | 103S2.047 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CP01 |  | TM140011XS047 | TM140011.105S1.047 | TM140011.105S1.047.FWD | BALE RECIEVING CONVEYOR 2 LOCAL START FWD | 105 S1 | Push Button | +CC01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | Andritz | +CC01 | 1400105S1.047 | 11105S1.047 | 105S1.047 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CP01 |  | TM140011XS047 | TM140011.105S2.047 | TM140011.105S2.047.REV | BALE RECIEVING CONVEYOR 2 LOCAL START REV | 105 S2 | Push Button | +CC01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | Andritz | +CC01 | 1400105S2.047 | 11105S2.047 | 105S2.047 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CP01 |  | TM140011XS048 | TM140011FC S04. 048 | TM140011FC S04. 048.ESTOP | BALE RECIEVING CONVEYOR E-STOP | FC S04 | E-STOP Push Button | +CC01 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | E-Stop | [11 empty] | 1 | Andritz | +CC01 | 1400 S04. 048 | 11 S04. 048 | FC S04. 048 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011XS049 | TM140011CP02 | TM1400111CP02 | FEEDING CONVEYOR LOCAL CONTROL PANEL | [31 empty] | 0 | Andritz |  | 1400 | 11 | CP | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CP02 |  | TM140011XS049 | TM140011S11 049 | TM140011S11 049.FWD | LOCAL JOG FWD | S11 | Push Button | +CP02 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | Andritz | 24VDC from +CP02 | 1400 049 | 11 049 | S 049 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CP02 |  | TM140011XS049 | TM140011S12 049 | TM140011S12 049.AUT | RELEASE AUTO START | S12 | Push Button | +CP02 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | Andritz | 24VDC from +CP02 | 1400 049 | 11 049 | S 049 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CP02 |  | TM140011XS049 | TM140011S9 049 | TM140011S9 049.L/R | LOCAL/DCS | S9 | Push Button | +CP02 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | Andritz | 24VDC from +CP02 | 1400 049 | 11 049 | S 049 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CP02 |  | TM140011XS049 | TM140011S12.4 049 | TM140011S12.4 049.AUTL | RELEASE AUTO START LAMP | S12.4 | Push Button | +CP02 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5 | Andritz | 24VDC from +CP02 | 14004 049 | 114 049 | 4 049 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CP03 |  | TM140011XS050 | TM140011S10 050 | TM140011S10 050.ESTOP | FEEDING CONVEYOR E-STOP | S10 | E-STOP Push Button | +CP02 | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | E-Stop | [11 empty] | 5 | Andritz | 24VDC from +CP02 | 1400 050 | 11 050 | S 050 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD003 |  | TM140011ZS053 | TM140011S11.1 053 | TM140011S11.1 053.DET | DETECTED METAL ALARM | S11.1 | Metal detector | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 | Andritz |  | 14001 053 | 111 053 | 1 053 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD003 |  | TM140011KS053 | TM140011S11.2 053 | TM140011S11.2 053.DET | DETECTED METAL WORKING | S11.1 | Metal detector | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 7 | Andritz |  | 14001 053 | 111 053 | 1 053 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD004 |  | TM140011TS054 | TM140011TS054 | TM140011TS054.H | NBKP #3 DEFLAKER OUTLET TEMPERATURE HIGH | TS | Temperature switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 100 | ˚C | [7 empty] | Temp. High | Not Temp. High | [10 empty] | 1 | Andritz |  | 1400 | 11 | TS | DI | ˚C
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS055 | TM140011SV055 | TM140011SV055 | NBKP #3 DEFLAKER FEED ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B |  |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS008 |  | TM140011HS055 | TM140011SV055.ZSC | TM140011SV055.GSC | NBKP #3 DEFLAKER FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS008 |  | TM140011HS055 | TM140011SV055.ZSO | TM140011SV055.GSO | NBKP #3 DEFLAKER FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS008 |  | TM140011HS055 | TM140011EV055 | TM140011EV055 | NBKP #3 DEFLAKER FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS057 | TM140011SV057 | TM140011SV057 | NBKP #3 DEFLAKER BYPASS ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B |  |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS008 |  | TM140011HS057 | TM140011SV057.ZSC | TM140011SV057.GSC | NBKP #3 DEFLAKER BYPASS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS008 |  | TM140011HS057 | TM140011SV057.ZSO | TM140011SV057.GSO | NBKP #3 DEFLAKER BYPASS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS008 |  | TM140011HS057 | TM140011EV057 | TM140011EV057 | NBKP #3 DEFLAKER BYPASS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS058 | TM140011SV058 | TM140011SV058 | SEALING WATER TO NBKP #3 DEFLAKER ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS008 |  | TM140011HS058 | TM140011SV058.ZSC | TM140011SV058.GSC | SEALING WATER TO NBKP #3 DEFLAKER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS008 |  | TM140011HS058 | TM140011SV058.ZSO | TM140011SV058.GSO | SEALING WATER TO NBKP #3 DEFLAKER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS008 |  | TM140011HS058 | TM140011EV058 | TM140011EV058 | SEALING WATER TO NBKP #3 DEFLAKER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD004 |  | TM140012FS059 | TM140012FS059 | TM140012FS059.L | SEALING WATER TO NBKP #3 DEFLAKER FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0.5 | 3 | l/min | [7 empty] | Flow L | Not Flow L | [10 empty] | 1 | Andritz |  | 1400 | 12 | FS | DI | l/min
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS061 | TM140011SV061 | TM140011SV061 | DILLUTION WATER TO NBKP #3 DEFLAKER FEED ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B |  |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS008 |  | TM140011HS061 | TM140011SV061.ZSC | TM140011SV061.GSC | DILLUTION WATER TO NBKP #3 DEFLAKER FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS008 |  | TM140011HS061 | TM140011SV061.ZSO | TM140011SV061.GSO | DILLUTION WATER TO NBKP #3 DEFLAKER FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS008 |  | TM140011HS061 | TM140011EV061 | TM140011EV061 | DILLUTION WATER TO NBKP #3 DEFLAKER FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD003 |  | TM140011GS071 | TM140011GS071.A | TM140011GS071.A | BALE RECEIVING CHAIN CONVEYOR POSITION | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC EXTERNAL | 2 | RR | [10 empty] | Front Position | Not Front Position | [10 empty] | 5 | Andritz |  | 1400 | 11 | A | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD003 |  | TM140011GS071 | TM140011GS071.B | TM140011GS071.B | BALE RECEIVING CHAIN CONVEYOR POSITION | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC EXTERNAL | 2 | RR | [10 empty] | Back Position | Not Back Position | [10 empty] | 5 | Andritz |  | 1400 | 11 | B | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD003 |  | TM140011GS072 | TM140011GS072.A | TM140011GS072.A | BALE CONVEYOR POSITION | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC EXTERNAL | 2 | RR | [10 empty] | Front Position | Not Front Position | [10 empty] | 5 | Andritz |  | 1400 | 11 | A | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD003 |  | TM140011GS072 | TM140011GS072.B | TM140011GS072.B | BALE CONVEYOR POSITION | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC EXTERNAL | 2 | RR | [10 empty] | Back Position | Not Back Position | [10 empty] | 5 | Andritz |  | 1400 | 11 | B | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD003 |  | TM140011GS073 | TM140011GS073.A | TM140011GS073.A | CHAIN CONVEYOR POSITION | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC EXTERNAL | 2 | RR | [10 empty] | Front Position | Not Front Position | [10 empty] | 5 | Andritz |  | 1400 | 11 | A | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD003 |  | TM140011GS073 | TM140011GS073.B | TM140011GS073.B | CHAIN CONVEYOR POSITION | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC EXTERNAL | 2 | RR | [10 empty] | Back Position | Not Back Position | [10 empty] | 5 | Andritz |  | 1400 | 11 | B | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD003 |  | TM140011FE080 | TM140011GS080 | TM140011GS080 | BALE RECEIVING SYSTEM | GS | Foot Switch | Field | DCS | DI | Dry Contact | 24 VDC EXTERNAL | 2 | RR | [10 empty] | Front Position | Not Front Position | [10 empty] | 7 | Andritz |  | 1400 | 11 | A | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD003 |  | TM140011FE081 | TM140011GS081 | TM140011GS081 | BALE RECEIVING SYSTEM | GS | Foot Switch | Field | DCS | DI | Dry Contact | 24 VDC EXTERNAL | 2 | RR | [10 empty] | Front Position | Not Front Position | [10 empty] | 7 | Andritz |  | 1400 | 11 | A | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 |  | TM140011PC101 | TM140011PT101 | TM140011PT101.MV | NBKP #3 REFINER #1 FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 5 | Bar.g | [19 empty] | 1 |  |  | 1400 | 11 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 | TM1400ASD004 | TM140011PC101 | TM140011PV101 | TM140011PV101.OUT | NBKP #3 REFINER #1 FEED PRESSURE CV SETPOINT | PV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 11 | PV | AO | %,bar
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011PC101 | TM140011PI101 | TM140011PI101.IND | NBKP #3 REFINER #1 FEED PRESSURE | PI | Local digital indicator | Field | DCS | AO | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 5 | Bar.g | [19 empty] | 1 | Andritz |  | 1400 | 11 | PI | AO | bar,Bar.g
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 |  | TM140011PI102 | TM140011PT102 | TM140011PT102.MV | NBKP #3 REFINER #1 OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1 | Andritz |  | 1400 | 11 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011PI102 | TM140011PI102 | TM140011PI102.IND | NBKP #3 REFINER #1 OUTLET PRESSURE | PI | Local digital indicator | Field | DCS | AO | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 10 | Bar.g | [19 empty] | 1 | Andritz |  | 1400 | 11 | PI | AO | bar,Bar.g
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011TIZ104 | TM140011TE104 |  | NBKP #3 REFINER #1 OUTLET TEMPERATURE | TE | Temperature sensor | Field | [28 empty] | B | Andritz |  | 1400 | 11 | TE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 |  | TM140011TIZ104 | TM140011TT104 | TM140011TT104.MV | NBKP #3 REFINER #1 OUTLET TEMPERATURE | TT | Temperature transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 150 | ˚C | [19 empty] | 1 | Andritz |  | 1400 | 11 | TT | AI | °C,℃,˚C
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD004 |  | TM140011TIZ104 | TM140011TS104 | TM140011TS104.H | NBKP #3 REFINER #1 OUTLET TEMPERATURE HIGH | TS | Temperature switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 150 | ˚C | [7 empty] | Temp. High | Not Temp. High | [10 empty] | 1 | Andritz |  | 1400 | 11 | TS | DI | ˚C
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS105 | TM140011SV105 | TM140011SV105 | NBKP #3 REFINER #1 FEED ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B |  |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS008 |  | TM140011HS105 | TM140011SV105.ZSC | TM140011SV105.GSC | NBKP #3 REFINER #1 FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS008 |  | TM140011HS105 | TM140011SV105.ZSO | TM140011SV105.GSO | NBKP #3 REFINER #1 FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS008 |  | TM140011HS105 | TM140011EV105 | TM140011EV105 | NBKP #3 REFINER #1 FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS107 | TM140011SV107 | TM140011SV107 | NBKP #3 REFINER #1 BYPASS ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B |  |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS008 |  | TM140011HS107 | TM140011SV107.ZSC | TM140011SV107.GSC | NBKP #3 REFINER #1 BYPASS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS008 |  | TM140011HS107 | TM140011SV107.ZSO | TM140011SV107.GSO | NBKP #3 REFINER #1 BYPASS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS008 |  | TM140011HS107 | TM140011EV107 | TM140011EV107 | NBKP #3 REFINER #1 BYPASS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS108 | TM140011SV108 | TM140011SV108 | SEALING WATER TO NBKP #3 REFINER #1 ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS108 | TM140011SV108.ZSC | TM140011SV108.GSC | SEALING WATER TO NBKP #3 REFINER #1 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS108 | TM140011SV108.ZSO | TM140011SV108.GSO | SEALING WATER TO NBKP #3 REFINER #1 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS108 | TM140011EV108 | TM140011EV108 | SEALING WATER TO NBKP #3 REFINER #1 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD004 |  | TM140011FS109 | TM140011FS109 | TM140011FS109.L | SEALING WATER TO NBKP #3 REFINER #1 FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0.5 | 3 | l/min | [7 empty] | Flow L | Not Flow L | [10 empty] | 1 | Andritz |  | 1400 | 11 | FS | DI | l/min
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD004 |  | TM140011GS110 | TM140011GS110.A | TM140011GS110.A.START | NBKP #3 REFINER #1 FILLINGS POSITION START | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Start | Start | [10 empty] | 1 | Andritz |  | 1400 | 11 | A | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD004 |  | TM140011GS110 | TM140011GS110.B | TM140011GS110.B.OPEN | NBKP #3 REFINER #1 FILLINGS POSITION OPEN | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 | Andritz |  | 1400 | 11 | B | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD004 |  | TM140011GS110 | TM140011GS110.C | TM140011GS110.C.SAF | NBKP #3 REFINER #1 FILLINGS POSITION SAFETY | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Safety | Safety | [10 empty] | 1 | Andritz |  | 1400 | 11 | C | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011EC111 | TM140011ET111 | TM140011ET111.MV | NBKP #3 REFINER #1 POWER | ET | Power transmitter | MCC | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | MCC | 0 | 800 | kW | [19 empty] | B |  |  | 1400 | 11 | ET | AI | kW
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011EC111 | TM140011EI111 | TM140011EI111.IND | NBKP #3 REFINER #1 POWER | EI | Local digital indicator | Field | DCS | AO | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 800 | kW | [19 empty] | 1 | Andritz |  | 1400 | 11 | EI | AO | kW
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011EFI112 | TM140011EX112 | TM140011EX112.SOF | NBKP #3 REFINING R1/R2 RATION | EX | DCS software function | DCS | DCS |  | Software function | [28 empty] | 1400 | 11 | EX | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011WC113 | TM140011WC113 | TM140011WC113.SOF | NBKP #3 REFINING POWER | WC | DCS software function | DCS | DCS |  | Software function | [25 empty] | B |  |  | 1400 | 11 | WC | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011FC116 | TM140011FE116 |  | NBKP #3 FROM REFINER FLOW | FE | Magnetic flow Sensor | Field | [31 empty] | 1400 | 11 | FE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA002 |  | TM140011FC116 | TM140011FT116 | TM140011FT116.MV | NBKP #3 FROM REFINER FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 0 | 4500 | l/min | [19 empty] | 1 |  |  | 1400 | 11 | FT | AI | l/min,kg/h,mc/h,t / hr,m3/hr
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA002 | TM1400ASD002 | TM140011FC116 | TM140011FV116 | TM140011FV116.OUT | NBKP #3 FROM REFINER FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 11 | FV | AO | %
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011FC117 | TM140011FE117 |  | NBKP #3 REFINING RECIRCULATION FLOW | FE | Magnetic flow Sensor | Field | [28 empty] | B |  |  | 1400 | 11 | FE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA002 |  | TM140011FC117 | TM140011FT117 | TM140011FT117.MV | NBKP #3 REFINING RECIRCULATION FLOW | FT | Magnetic flow transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 0 | 4000 | l/min | [19 empty] | 1 |  |  | 1400 | 11 | FT | AI | l/min,kg/h,mc/h,t / hr,m3/hr
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA002 | TM1400ASD002 | TM140011FC117 | TM140011FV117 | TM140011FV117.OUT | NBKP #3 REFINING RECIRCULATION FLOW CV SETPOINT | FV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 11 | FV | AO | %
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS119 | TM140011SV119 | TM140011SV119 | NBKP #3 RECIRCULATION LINE FLUSHING ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS119 | TM140011SV119.ZSC | TM140011SV119.GSC | NBKP #3 RECIRCULATION LINE FLUSHING ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS119 | TM140011SV119.ZSO | TM140011SV119.GSO | NBKP #3 RECIRCULATION LINE FLUSHING ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS119 | TM140011EV119 | TM140011EV119 | NBKP #3 RECIRCULATION LINE FLUSHING ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011XS120 | TM140011CB01 | TM140011CB01 | NBKP #3 REFINER #1 CONTROL | CB | Local Control Box | Field |  |  |  | 230VAC | [24 empty] | 7 | Andritz |  | 1400 | 11 | CB |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS120 | TM140011H11 120 | TM140011H11 120.RUN/F | NBKP #3 REFINER #1 MOTOR RUN / FAULT | H11 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Run | Run | [10 empty] | 1 | Andritz |  | 1400 120 | 11 120 | H 120 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS120 | TM140011H21 120 | TM140011H21 120.L/F | NBKP #3 REFINER #1 LOAD / FAULT | H21 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Load | Load | [10 empty] | 1 | Andritz |  | 1400 120 | 11 120 | H 120 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS120 | TM140011H22 120 | TM140011H22 120.REL/F | NBKP #3 REFINER #1 RELEASE / FAULT | H22 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Release | Release | [10 empty] | 1 | Andritz |  | 1400 120 | 11 120 | H 120 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS120 | TM140011H23 120 | TM140011H23 120.FAULT | NBKP #3 REFINER #1 FAULT | H23 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Fault | Fault | [10 empty] | 1 | Andritz |  | 1400 120 | 11 120 | H 120 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS120 | TM140011S10 120 | TM140011S10 120.ESTOP | NBKP #3 REFINER #1 PANEL E - STOP | S10 | E - Stop Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | E - Stop | Not E - Stop | [10 empty] | 1 | Andritz |  | 1400 120 | 11 120 | S 120 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS120 | TM140011S11 120 | TM140011S11 120.START | NBKP #3 REFINER #1 START | S11 | Illuminated Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Start | Start | [10 empty] | 1 | Andritz |  | 1400 120 | 11 120 | S 120 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS120 | TM140011S12 120 | TM140011S12 120.STOP | NBKP #3 REFINER #1 STOP | S12 | Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Stop | Not Stop | [10 empty] | 1 | Andritz |  | 1400 120 | 11 120 | S 120 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS120 | TM140011S20 120 | TM140011S20 120.L/D | OPERATING MODE SELECT SWITCH - LOCAL/DCS | S20 | Select Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | DCS | Local | [10 empty] | 1 | Andritz |  | 1400 120 | 11 120 | S 120 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS120 | TM140011S21 120 | TM140011S21 120.LOAD | NBKP #3 REFINER #1 LOAD | S21 | Illuminated Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Load | Load | [10 empty] | 1 | Andritz |  | 1400 120 | 11 120 | S 120 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS120 | TM140011S22 120 | TM140011S22 120.RELEASE | NBKP #3 REFINER #1 RELEASE | S22 | Illuminated Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Release | Release | [10 empty] | 1 | Andritz |  | 1400 120 | 11 120 | S 120 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS120 | TM140011S23 120 | TM140011S23 120.FAST | NBKP #3 REFINER #1 FAST | S23 | Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Fast | Fast | [10 empty] | 1 | Andritz |  | 1400 120 | 11 120 | S 120 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS120 | TM140011S24 120 | TM140011S24 120.TEST | NBKP #3 REFINER #1 CB LAMP TEST | S24 | Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Lamp Test | Lamp Test | [10 empty] | 1 | Andritz |  | 1400 120 | 11 120 | S 120 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS122 | TM140011SV122 | TM140011SV122 | REFINER1 NBKP#3 INLET FLUSH ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B |  |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS122 | TM140011SV122.ZSC | TM140011SV122.GSC | REFINER1 NBKP#3 INLET FLUSH ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS122 | TM140011SV122.ZSO | TM140011SV122.GSO | REFINER1 NBKP#3 INLET FLUSH ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS122 | TM140011EV122 | TM140011EV122 | REFINER1 NBKP#3 INLET FLUSH ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS123 | TM140011SV123 | TM140011SV123 | REFINER 1&2 NBKP#3 ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B |  |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS123 | TM140011SV123.ZSC | TM140011SV123.GSC | REFINER 1&2 NBKP#3 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS123 | TM140011SV123.ZSO | TM140011SV123.GSO | REFINER 1&2 NBKP#3 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS123 | TM140011EV123 | TM140011EV123 | REFINER 1&2 NBKP#3 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011AI132 | TM140011AE132 |  | NBKP #3 REFINED OUTLETFREENESS | AE | Freeness sensor | Field | [31 empty] | 1400 | 11 | AE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 |  | TM140011AI132 | TM140011AT132 | TM140011AT132.MV | NBKP #3 REFINED OUTLETFREENESS | AT | Freeness transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 15 | 750 | ml CSF | [19 empty] | 1 |  |  | 1400 | 11 | AT | AI | Ph,ml CSF
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD004 |  | TM140011AI132 | TM140011AS132 | TM140011AS132.MV | NBKP #3 REFINED OUTLETFREENESS | AS | Freeness transmitter Stop Sampling | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  |  | 1400 | 11 | AS | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 |  | TM140011PC151 | TM140011PT151 | TM140011PT151.MV | NBKP #3 REFINER #2 FEED PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 5 | Bar.g | [19 empty] | 1 |  |  | 1400 | 11 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 | TM1400ASD004 | TM140011PC151 | TM140011PV151 | TM140011PV151.OUT | NBKP #3 REFINER #2 FEED PRESSURE CV SETPOINT | PV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 11 | PV | AO | %,bar
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB02 |  | TM140011PC151 | TM140011PI151 | TM140011PI151.IND | NBKP #3 REFINER #2 FEED PRESSURE | PI | Local digital indicator | Field | DCS | AO | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 5 | Bar.g | [19 empty] | 1 | Andritz |  | 1400 | 11 | PI | AO | bar,Bar.g
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 |  | TM140011PIZ152 | TM140011PT152 | TM140011PT152.MV | NBKP #3 REFINER #2 OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1 | Andritz |  | 1400 | 11 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB02 |  | TM140011PIZ152 | TM140011PI152 | TM140011PI152.IND | NBKP #3 REFINER #2 OUTLET PRESSURE | PI | Local digital indicator | Field | DCS | AO | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 10 | Bar.g | [19 empty] | 1 | Andritz |  | 1400 | 11 | PI | AO | bar,Bar.g
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011TIZ154 | TM140011TE154 |  | NBKP #3 REFINER #2 OUTLET TEMPERATURE | TE | Temperature sensor | Field | [28 empty] | B | Andritz |  | 1400 | 11 | TE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA003 |  | TM140011TIZ154 | TM140011TT154 | TM140011TT154.MV | NBKP #3 REFINER #2 OUTLET TEMPERATURE | TT | Temperature transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 150 | ˚C | [19 empty] | 1 | Andritz |  | 1400 | 11 | TT | AI | °C,℃,˚C
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD004 |  | TM140011TIZ154 | TM140011TS154 | TM140011TS154.H | NBKP #3 REFINER #2 OUTLET TEMPERATURE HIGH | TS | Temperature switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0 | 150 | ˚C | [7 empty] | Temp. High | Not Temp. High | [10 empty] | 1 | Andritz |  | 1400 | 11 | TS | DI | ˚C
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS155 | TM140011SV155 | TM140011SV155 | NBKP #3 REFINER #2 FEED ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B |  |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS155 | TM140011SV155.ZSC | TM140011SV155.GSC | NBKP #3 REFINER #2 FEED ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS155 | TM140011SV155.ZSO | TM140011SV155.GSO | NBKP #3 REFINER #2 FEED ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS155 | TM140011EV155 | TM140011EV155 | NBKP #3 REFINER #2 FEED ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS156 | TM140011SV156 | TM140011SV156 | NBKP #3 REFINER #2 ACCEPT ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B |  |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS156 | TM140011SV156.ZSC | TM140011SV156.GSC | NBKP #3 REFINER #2 ACCEPT ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS156 | TM140011SV156.ZSO | TM140011SV156.GSO | NBKP #3 REFINER #2 ACCEPT ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS156 | TM140011EV156 | TM140011EV156 | NBKP #3 REFINER #2 ACCEPT ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS157 | TM140011SV157 | TM140011SV157 | NBKP #3 REFINER #2 BYPASS ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B |  |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS157 | TM140011SV157.ZSC | TM140011SV157.GSC | NBKP #3 REFINER #2 BYPASS ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS157 | TM140011SV157.ZSO | TM140011SV157.GSO | NBKP #3 REFINER #2 BYPASS ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS157 | TM140011EV157 | TM140011EV157 | NBKP #3 REFINER #2 BYPASS ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS158 | TM140011SV158 | TM140011SV158 | SEALING WATER TO NBKP #3 REFINER #2 ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS158 | TM140011SV158.ZSC | TM140011SV158.GSC | SEALING WATER TO NBKP #3 REFINER #2 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS158 | TM140011SV158.ZSO | TM140011SV158.GSO | SEALING WATER TO NBKP #3 REFINER #2 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS158 | TM140011EV158 | TM140011EV158 | SEALING WATER TO NBKP #3 REFINER #2 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD004 |  | TM140011FS159 | TM140011FS159 | TM140011FS159.L | SEALING WATER TO NBKP #3 REFINER #2 FLOW L | FS | Flow switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | 0.5 | 3 | l/min | [7 empty] | Flow L | Not Flow L | [10 empty] | 1 | Andritz |  | 1400 | 11 | FS | DI | l/min
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD004 |  | TM140011GS160 | TM140011GS160.A | TM140011GS160.A.START | NBKP #3 REFINER #2 FILLINGS POSITION START | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Start | Start | [10 empty] | 1 | Andritz |  | 1400 | 11 | A | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD004 |  | TM140011GS160 | TM140011GS160.B | TM140011GS160.B.OPEN | NBKP #3 REFINER #2 FILLINGS POSITION OPEN | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 | Andritz |  | 1400 | 11 | B | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD004 |  | TM140011GS160 | TM140011GS160.C | TM140011GS160.C.SAF | NBKP #3 REFINER #2 FILLINGS POSITION SAFETY | GS | Limit switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Safety | Safety | [10 empty] | 1 | Andritz |  | 1400 | 11 | C | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011EC161 | TM140011ET161 | TM140011ET161.MV | NBKP #3 REFINER #2 POWER | ET | Power transmitter | MCC | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | MCC | 0 | 800 | kW | [19 empty] | B |  |  | 1400 | 11 | ET | AI | kW
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB02 |  | TM140011EC161 | TM140011EI161 | TM140011EI161.IND | NBKP #3 REFINER #2 POWER | EI | Local digital indicator | Field | DCS | AO | 4-20 mA HART | 24 VDC | 2+2 | RR | 0 | 800 | kW | [19 empty] | 1 | Andritz |  | 1400 | 11 | EI | AO | kW
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS162 | TM140011SV162 | TM140011SV162 | REFINER 2 NBKP#3 INLET FLUSH ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B |  |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS162 | TM140011SV162.ZSC | TM140011SV162.GSC | REFINER 2 NBKP#3 INLET FLUSH ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS162 | TM140011SV162.ZSO | TM140011SV162.GSO | REFINER 2 NBKP#3 INLET FLUSH ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS009 |  | TM140011HS162 | TM140011EV162 | TM140011EV162 | REFINER 2 NBKP#3 INLET FLUSH ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011XS170 | TM140011CB01 | TM110011CB01 | NBKP #3 REFINER #2 CONTROL | CB | Local Control Box | Field |  |  |  | 230VAC | [24 empty] | 7 | Andritz |  | 1400 | 11 | CB |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS170 | TM140011H11 170 | TM140011H11 170.RUN/F | NBKP #3 REFINER #2 MOTOR RUN / FAULT | H11 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Run | Run | [10 empty] | 1 | Andritz |  | 1400 170 | 11 170 | H 170 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS170 | TM140011H21 170 | TM140011H21 170.L/F | NBKP #3 REFINER #2 LOAD / FAULT | H21 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Load | Load | [10 empty] | 1 | Andritz |  | 1400 170 | 11 170 | H 170 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS170 | TM140011H22 170 | TM140011H22 170.REL/F | NBKP #3 REFINER #2 RELEASE / FAULT | H22 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Release | Release | [10 empty] | 1 | Andritz |  | 1400 170 | 11 170 | H 170 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS170 | TM140011H23 170 | TM140011H23 170.FAULT | NBKP #3 REFINER #2 FAULT | H23 | Indicator light | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Fault | Fault | [10 empty] | 1 | Andritz |  | 1400 170 | 11 170 | H 170 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS170 | TM140011S10 170 | TM140011S10 170.ESTOP | NBKP #3 REFINER #2 PANEL E - STOP | S10 | E - Stop Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | E - Stop | Not E - Stop | [10 empty] | 1 | Andritz |  | 1400 170 | 11 170 | S 170 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS170 | TM140011S11 170 | TM140011S11 170.START | NBKP #3 REFINER #2 START | S11 | Illuminated Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Start | Start | [10 empty] | 1 | Andritz |  | 1400 170 | 11 170 | S 170 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS170 | TM140011S12 170 | TM140011S12 170.STOP | NBKP #3 REFINER #2 STOP | S12 | Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Stop | Not Stop | [10 empty] | 1 | Andritz |  | 1400 170 | 11 170 | S 170 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS170 | TM140011S20 170 | TM140011S20 170.L/D | OPERATING MODE SELECT SWITCH - LOCAL/DCS | S20 | Select Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | DCS | Local | [10 empty] | 1 | Andritz |  | 1400 170 | 11 170 | S 170 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS170 | TM140011S21 170 | TM140011S21 170.LOAD | NBKP #3 REFINER #2 LOAD | S21 | Illuminated Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Load | Load | [10 empty] | 1 | Andritz |  | 1400 170 | 11 170 | S 170 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS170 | TM140011S22 170 | TM140011S22 170.RELEASE | NBKP #3 REFINER #2 RELEASE | S22 | Illuminated Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Release | Release | [10 empty] | 1 | Andritz |  | 1400 170 | 11 170 | S 170 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS170 | TM140011S23 170 | TM140011S23 170.FAST | NBKP #3 REFINER #2 FAST | S23 | Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Fast | Fast | [10 empty] | 1 | Andritz |  | 1400 170 | 11 170 | S 170 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM140011CB01 |  | TM140011XS170 | TM140011S24 170 | TM140011S24 170.TEST | NBKP #3 REFINER #2 CB LAMP TEST | S24 | Push Button | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Lamp Test | Lamp Test | [10 empty] | 1 | Andritz |  | 1400 170 | 11 170 | S 170 | #N/A | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS141 | TM140011SV141 | TM140011SV141 | NBKP #3 REFINED TO NBKP #3 REFINER TOWER #1 ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS141 | TM140011SV141.ZSC | TM140011SV141.GSC | NBKP #3 REFINED TO NBKP #3 REFINER TOWER #1 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS141 | TM140011SV141.ZSO | TM140011SV141.GSO | NBKP #3 REFINED TO NBKP #3 REFINER TOWER #1 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS141 | TM140011EV141 | TM140011EV141 | NBKP #3 REFINED TO NBKP #3 REFINER TOWER #1 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS142 | TM140011SV142 | TM140011SV142 | NBKP #3 REFINED TO NBKP #3 REFINER TOWER #2 ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS142 | TM140011SV142.ZSC | TM140011SV142.GSC | NBKP #3 REFINED TO NBKP #3 REFINER TOWER #2 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS142 | TM140011SV142.ZSO | TM140011SV142.GSO | NBKP #3 REFINED TO NBKP #3 REFINER TOWER #2 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS142 | TM140011EV142 | TM140011EV142 | NBKP #3 REFINED TO NBKP #3 REFINER TOWER #2 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS143 | TM140011SV143 | TM140011SV143 | NBKP #3 REFINED TO SP # 2 BROKE TOWER ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS143 | TM140011SV143.ZSC | TM140011SV143.GSC | NBKP #3 REFINED TO SP # 2 BROKE TOWER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS143 | TM140011SV143.ZSO | TM140011SV143.GSO | NBKP #3 REFINED TO SP # 2 BROKE TOWER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS004 |  | TM140011HS143 | TM140011EV143 | TM140011EV143 | NBKP #3 REFINED TO SP # 2 BROKE TOWER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS144 | TM140011SV144 | TM140011SV144 | NBKP #1 REFINED TOWER PUMP4 OUTLET TO NBKP #3 REFINER TOWER #1 ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | 0 |  |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS144 | TM140011SV144.ZSC | TM140011SV144.GSC | NBKP #1 REFINED TOWER PUMP4 OUTLET TO NBKP #3 REFINER TOWER #1 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS144 | TM140011SV144.ZSO | TM140011SV144.GSO | NBKP #1 REFINED TOWER PUMP4 OUTLET TO NBKP #3 REFINER TOWER #1 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS144 | TM140011EV144 | TM140011EV144 | NBKP #1 REFINED TOWER PUMP4 OUTLET TO NBKP #3 REFINER TOWER #1 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS145 | TM140011SV145 | TM140011SV145 | NBKP #1 REFINED TOWER PUMP4 OUTLET TO NBKP #3 REFINER TOWER #2 ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | 0 |  |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS145 | TM140011SV145.ZSC | TM140011SV145.GSC | NBKP #1 REFINED TOWER PUMP4 OUTLET TO NBKP #3 REFINER TOWER #2 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS145 | TM140011SV145.ZSO | TM140011SV145.GSO | NBKP #1 REFINED TOWER PUMP4 OUTLET TO NBKP #3 REFINER TOWER #2 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS145 | TM140011EV145 | TM140011EV145 | NBKP #1 REFINED TOWER PUMP4 OUTLET TO NBKP #3 REFINER TOWER #2 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS146 | TM140011SV146 | TM140011SV146 | NBKP #2 REFINED TOWER PUMP4 OUTLET TO NBKP #3 REFINER TOWER #1 ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | 0 |  |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS146 | TM140011SV146.ZSC | TM140011SV146.GSC | NBKP #2 REFINED TOWER PUMP4 OUTLET TO NBKP #3 REFINER TOWER #1 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS146 | TM140011SV146.ZSO | TM140011SV146.GSO | NBKP #2 REFINED TOWER PUMP4 OUTLET TO NBKP #3 REFINER TOWER #1 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS146 | TM140011EV146 | TM140011EV146 | NBKP #2 REFINED TOWER PUMP4 OUTLET TO NBKP #3 REFINER TOWER #1 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS147 | TM140011SV147 | TM140011SV147 | NBKP #2 REFINED TOWER PUMP4 OUTLET TO NBKP #3 REFINER TOWER #2 ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | 0 |  |  | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS147 | TM140011SV147.ZSC | TM140011SV147.GSC | NBKP #2 REFINED TOWER PUMP4 OUTLET TO NBKP #3 REFINER TOWER #2 ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS147 | TM140011SV147.ZSO | TM140011SV147.GSO | NBKP #2 REFINED TOWER PUMP4 OUTLET TO NBKP #3 REFINER TOWER #2 ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS147 | TM140011EV147 | TM140011EV147 | NBKP #2 REFINED TOWER PUMP4 OUTLET TO NBKP #3 REFINER TOWER #2 ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 |  | TM140011LI440 | TM140011LT440 | TM140011LT440.MV | NBKP #3 REFINER TOWER #1 LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 9000 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1 |  |  | 1400 | 11 | LT | AI | %,mm
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS441 | TM140011SV441 | TM140011SV441 | NBKP #3 REFINER TOWER #1 PUMP 1 INLET ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS441 | TM140011SV441.ZSC | TM140011SV441.GSC | NBKP #3 REFINER TOWER #1 PUMP 1 INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS441 | TM140011SV441.ZSO | TM140011SV441.GSO | NBKP #3 REFINER TOWER #1 PUMP 1 INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS441 | TM140011EV441 | TM140011EV441 | NBKP #3 REFINER TOWER #1 PUMP 1 INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NC442 | TM140011NE442 |  | NBKP #3 REFINER TOWER #1 PUMP 1 OUTPUT CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230VAC | [24 empty] | B |  |  | 1400 | 11 | NE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 |  | TM140011NC442 | TM140011NT442 | TM140011NT442.MV | NBKP #3 REFINER TOWER #1 PUMP 1 OUTPUT CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 2 | 6 | %C | [19 empty] | 1 |  |  | 1400 | 11 | NT | AI | %C
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD001 |  | TM140011NC442 | TM140011NS442 | TM140011NS442.MV | NBKP #3 REFINER TOWER #1 PUMP 1 OUTPUT CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  |  | 1400 | 11 | NS | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 | TM1400ASD001 | TM140011NC442 | TM140011NV442 | TM140011NV442.OUT | NBKP #3 REFINER TOWER #1 PUMP 1 OUTPUT CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 11 | NV | AO | %
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 |  | TM140011PC443 | TM140011PT443 | TM140011PT443.MV | NBKP #3 REFINER TOWER #1 PUMP 1 OUTPUT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  |  | 1400 | 11 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS451 | TM140011SV451 | TM140011SV451 | NBKP #3 REFINER TOWER #1 PUMP 2 INLET ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS451 | TM140011SV451.ZSC | TM140011SV451.GSC | NBKP #3 REFINER TOWER #1 PUMP 2 INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS451 | TM140011SV451.ZSO | TM140011SV451.GSO | NBKP #3 REFINER TOWER #1 PUMP 2 INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS451 | TM140011EV451 | TM140011EV451 | NBKP #3 REFINER TOWER #1 PUMP 2 INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NC452 | TM140011NE452 |  | NBKP #3 REFINER TOWER #1 PUMP 2 OUTPUT CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230VAC | [24 empty] | B |  |  | 1400 | 11 | NE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 |  | TM140011NC452 | TM140011NT452 | TM140011NT452.MV | NBKP #3 REFINER TOWER #1 PUMP 2 OUTPUT CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 2 | 6 | %C | [19 empty] | 1 |  |  | 1400 | 11 | NT | AI | %C
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD001 |  | TM140011NC452 | TM140011NS452 | TM140011NS452.MV | NBKP #3 REFINER TOWER #1 PUMP 2 OUTPUT CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  |  | 1400 | 11 | NS | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 | TM1400ASD001 | TM140011NC452 | TM140011NV452 | TM140011NV452.OUT | NBKP #3 REFINER TOWER #1 PUMP 2 OUTPUT CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 11 | NV | AO | %
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 |  | TM140011PC453 | TM140011PT453 | TM140011PT453.MV | NBKP #3 REFINER TOWER #1 PUMP 2 OUTPUT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  |  | 1400 | 11 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS461 | TM140011SV461 | TM140011SV461 | NBKP #3 REFINER TOWER #1 PUMP 3 INLET ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS461 | TM140011SV461.ZSC | TM140011SV461.GSC | NBKP #3 REFINER TOWER #1 PUMP 3 INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS461 | TM140011SV461.ZSO | TM140011SV461.GSO | NBKP #3 REFINER TOWER #1 PUMP 3 INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS461 | TM140011EV461 | TM140011EV461 | NBKP #3 REFINER TOWER #1 PUMP 3 INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NC462 | TM140011NE462 |  | NBKP #3 REFINER TOWER #1 PUMP 3 OUTPUT CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230VAC | [24 empty] | B |  |  | 1400 | 11 | NE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 |  | TM140011NC462 | TM140011NT462 | TM140011NT462.MV | NBKP #3 REFINER TOWER #1 PUMP 3 OUTPUT CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 2 | 6 | %C | [19 empty] | 1 |  |  | 1400 | 11 | NT | AI | %C
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD001 |  | TM140011NC462 | TM140011NS462 | TM140011NS462.MV | NBKP #3 REFINER TOWER #1 PUMP 3 OUTPUT CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  |  | 1400 | 11 | NS | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 | TM1400ASD001 | TM140011NC462 | TM140011NV462 | TM140011NV462.OUT | NBKP #3 REFINER TOWER #1 PUMP 3 OUTPUT CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 11 | NV | AO | %
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 |  | TM140011PC463 | TM140011PT463 | TM140011PT463.MV | NBKP #3 REFINER TOWER #1 PUMP 3 OUTPUT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  |  | 1400 | 11 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS471 | TM140011SV471 | TM140011SV471 | NBKP #3 REFINER TOWER #1 PUMP 4 INLET ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS471 | TM140011SV471.ZSC | TM140011SV471.GSC | NBKP #3 REFINER TOWER #1 PUMP 4 INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS471 | TM140011SV471.ZSO | TM140011SV471.GSO | NBKP #3 REFINER TOWER #1 PUMP 4 INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS002 |  | TM140011HS471 | TM140011EV471 | TM140011EV471 | NBKP #3 REFINER TOWER #1 PUMP 4 INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NC472 | TM140011NE472 |  | NBKP #3 REFINER TOWER #1 PUMP 4 OUTPUT CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230VAC | [24 empty] | B |  |  | 1400 | 11 | NE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 |  | TM140011NC472 | TM140011NT472 | TM140011NT472.MV | NBKP #3 REFINER TOWER #1 PUMP 4 OUTPUT CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 2 | 6 | %C | [19 empty] | 1 |  |  | 1400 | 11 | NT | AI | %C
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD001 |  | TM140011NC472 | TM140011NS472 | TM140011NS472.MV | NBKP #3 REFINER TOWER #1 PUMP 4 OUTPUT CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  |  | 1400 | 11 | NS | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 | TM1400ASD001 | TM140011NC472 | TM140011NV472 | TM140011NV472.OUT | NBKP #3 REFINER TOWER #1 PUMP 4 OUTPUT CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 11 | NV | AO | %
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 |  | TM140011PC473 | TM140011PT473 | TM140011PT473.MV | NBKP #3 REFINER TOWER #1 PUMP 4 OUTPUT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  |  | 1400 | 11 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 |  | TM140011LI540 | TM140011LT540 | TM140011LT540.MV | NBKP #3 REFINER TOWER #2 LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 9000 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1 |  |  | 1400 | 11 | LT | AI | %,mm
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS541 | TM140011SV541 | TM140011SV541 | NBKP #3 REFINER TOWER #2 PUMP 1 INLET ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS541 | TM140011SV541.ZSC | TM140011SV541.GSC | NBKP #3 REFINER TOWER #2 PUMP 1 INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS541 | TM140011SV541.ZSO | TM140011SV541.GSO | NBKP #3 REFINER TOWER #2 PUMP 1 INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS541 | TM140011EV541 | TM140011EV541 | NBKP #3 REFINER TOWER #2 PUMP 1 INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NC542 | TM140011NE542 |  | NBKP #3 REFINER TOWER #2 PUMP 1 OUTPUT CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230VAC | [24 empty] | B |  |  | 1400 | 11 | NE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 |  | TM140011NC542 | TM140011NT542 | TM140011NT542.MV | NBKP #3 REFINER TOWER #2 PUMP 1 OUTPUT CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 2 | 6 | %C | [19 empty] | 1 |  |  | 1400 | 11 | NT | AI | %C
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD001 |  | TM140011NC542 | TM140011NS542 | TM140011NS542.MV | NBKP #3 REFINER TOWER #2 PUMP 1 OUTPUT CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  |  | 1400 | 11 | NS | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 | TM1400ASD002 | TM140011NC542 | TM140011NV542 | TM140011NV542.OUT | NBKP #3 REFINER TOWER #2 PUMP 1 OUTPUT CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 11 | NV | AO | %
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 |  | TM140011PC543 | TM140011PT543 | TM140011PT543.MV | NBKP #3 REFINER TOWER #2 PUMP 1 OUTPUT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  |  | 1400 | 11 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS551 | TM140011SV551 | TM140011SV551 | NBKP #3 REFINER TOWER #2 PUMP 2 INLET ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS551 | TM140011SV551.ZSC | TM140011SV551.GSC | NBKP #3 REFINER TOWER #2 PUMP 2 INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS551 | TM140011SV551.ZSO | TM140011SV551.GSO | NBKP #3 REFINER TOWER #2 PUMP 2 INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS551 | TM140011EV551 | TM140011EV551 | NBKP #3 REFINER TOWER #2 PUMP 2 INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NC552 | TM140011NE552 |  | NBKP #3 REFINER TOWER #2 PUMP 2 OUTPUT CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230VAC | [24 empty] | B |  |  | 1400 | 11 | NE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 |  | TM140011NC552 | TM140011NT552 | TM140011NT552.MV | NBKP #3 REFINER TOWER #2 PUMP 2 OUTPUT CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 2 | 6 | %C | [19 empty] | 1 |  |  | 1400 | 11 | NT | AI | %C
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD001 |  | TM140011NC552 | TM140011NS552 | TM140011NS552.MV | NBKP #3 REFINER TOWER #2 PUMP 2 OUTPUT CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  |  | 1400 | 11 | NS | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 | TM1400ASD002 | TM140011NC552 | TM140011NV552 | TM140011NV552.OUT | NBKP #3 REFINER TOWER #2 PUMP 2 OUTPUT CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 11 | NV | AO | %
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 |  | TM140011PC553 | TM140011PT553 | TM140011PT553.MV | NBKP #3 REFINER TOWER #2 PUMP 2 OUTPUT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  |  | 1400 | 11 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS561 | TM140011SV561 | TM140011SV561 | NBKP #3 REFINER TOWER #2 PUMP 3 INLET ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS561 | TM140011SV561.ZSC | TM140011SV561.GSC | NBKP #3 REFINER TOWER #2 PUMP 3 INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS561 | TM140011SV561.ZSO | TM140011SV561.GSO | NBKP #3 REFINER TOWER #2 PUMP 3 INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS561 | TM140011EV561 | TM140011EV561 | NBKP #3 REFINER TOWER #2 PUMP 3 INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NC562 | TM140011NE562 |  | NBKP #3 REFINER TOWER #2 PUMP 3 OUTPUT CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230VAC | [24 empty] | B |  |  | 1400 | 11 | NE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 |  | TM140011NC562 | TM140011NT562 | TM140011NT562.MV | NBKP #3 REFINER TOWER #2 PUMP 3 OUTPUT CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 2 | 6 | %C | [19 empty] | 1 |  |  | 1400 | 11 | NT | AI | %C
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD001 |  | TM140011NC562 | TM140011NS562 | TM140011NS562.MV | NBKP #3 REFINER TOWER #2 PUMP 3 OUTPUT CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  |  | 1400 | 11 | NS | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 | TM1400ASD002 | TM140011NC562 | TM140011NV562 | TM140011NV562.OUT | NBKP #3 REFINER TOWER #2 PUMP 3 OUTPUT CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 11 | NV | AO | %
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 |  | TM140011PC563 | TM140011PT563 | TM140011PT563.MV | NBKP #3 REFINER TOWER #2 PUMP 3 OUTPUT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  |  | 1400 | 11 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011HS571 | TM140011SV571 | TM140011SV571 | NBKP #3 REFINER TOWER #2 PUMP 4 INLET ON/OFF VALVE | SV | On/Off Valve | Field | [31 empty] | 1400 | 11 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS571 | TM140011SV571.ZSC | TM140011SV571.GSC | NBKP #3 REFINER TOWER #2 PUMP 4 INLET ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 11 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS571 | TM140011SV571.ZSO | TM140011SV571.GSO | NBKP #3 REFINER TOWER #2 PUMP 4 INLET ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 11 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBS003 |  | TM140011HS571 | TM140011EV571 | TM140011EV571 | NBKP #3 REFINER TOWER #2 PUMP 4 INLET ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 11 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NC572 | TM140011NE572 |  | NBKP #3 REFINER TOWER #2 PUMP 4 OUTPUT CONSISTENCY | NE | Rotary Consistency Sensor | Field |  |  |  | 230VAC | [24 empty] | B |  |  | 1400 | 11 | NE |  | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 |  | TM140011NC572 | TM140011NT572 | TM140011NT572.MV | NBKP #3 REFINER TOWER #2 PUMP 4 OUTPUT CONSISTENCY | NT | Rotary Consistency Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 2 | 6 | %C | [19 empty] | 1 |  |  | 1400 | 11 | NT | AI | %C
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBD001 |  | TM140011NC572 | TM140011NS572 | TM140011NS572.MV | NBKP #3 REFINER TOWER #2 PUMP 4 OUTPUT CONSISTENCY | NS | Rotary Consistency Transmitter Stop | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 1 |  |  | 1400 | 11 | NS | DO | #N/A
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 | TM1400ASD002 | TM140011NC572 | TM140011NV572 | TM140011NV572.OUT | NBKP #3 REFINER TOWER #2 PUMP 4 OUTPUT CONSISTENCY CV SETPOINT | NV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 11 | NV | AO | %
P-OKITM07-10-302-07-PID-4643 | TM140011 | TM1400JBA001 |  | TM140011PC573 | TM140011PT573 | TM140011PT573.MV | NBKP #3 REFINER TOWER #2 PUMP 4 OUTPUT PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  |  | 1400 | 11 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
| WHITE WATER AND FRESH WATER | [43 empty] | #N/A | #N/A
P-OKITM07-10-302-07-PID-4644 | TM140021 | TM1400JBA002 |  | TM140021LC001 | TM140021LT001 | TM140021LT001.MV | SP DILUTION COLLECTION TOWER LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 9500 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1 |  |  | 1400 | 21 | LT | AI | %,mm
P-OKITM07-10-302-07-PID-4644 | TM140021 | TM1400JBA002 | TM1400ASD003 | TM140021LC001 | TM140021LV001 | TM140021LV001.OUT | SP DILUTION COLLECTION TOWER LEVEL CV SETPOINT | LV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 21 | LV | AO | %
P-OKITM07-10-302-07-PID-4644 | TM140021 | TM1400JBA002 |  | TM140021PC002 | TM140021PT002 | TM140021PT002.MV | PULPER W.W PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 4 | Bar.g | [19 empty] | 1 |  |  | 1400 | 21 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4644 | TM140021 | TM1400JBA002 |  | TM140021PC005 | TM140021PT005 | TM140021PT005.MV | LBKP & NBKP CRC & FLUSHING PUMP OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  |  | 1400 | 21 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4644 | TM140021 |  |  | TM140021HS012 | TM140021SV012 | TM140021SV012 | OVER FLOW PUMP OUTLET TO SP 1 DILUTION COLLECTION TOWER ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B |  |  | 1400 | 21 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4644 | TM140021 | TM1400JBS011 |  | TM140021HS012 | TM140021SV012.ZSC | TM140021SV012.GSC | OVER FLOW PUMP OUTLET TO SP 1 DILUTION COLLECTION TOWER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 21 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4644 | TM140021 | TM1400JBS011 |  | TM140021HS012 | TM140021SV012.ZSO | TM140021SV012.GSO | OVER FLOW PUMP OUTLET TO SP 1 DILUTION COLLECTION TOWER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 21 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4644 | TM140021 | TM1400JBS011 |  | TM140021HS012 | TM140021EV012 | TM140021EV012 | OVER FLOW PUMP OUTLET TO SP 1 DILUTION COLLECTION TOWER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 21 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4644 | TM140021 |  |  | TM140021HS013 | TM140021SV013 | TM140021SV013 | OVER FLOW PUMP OUTLET TO W.W BUFFER TOWER ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B |  |  | 1400 | 21 | SV | DO | #N/A
P-OKITM07-10-302-07-PID-4644 | TM140021 | TM1400JBS011 |  | TM140021HS013 | TM140021SV013.ZSC | TM140021SV013.GSC | OVER FLOW PUMP OUTLET TO W.W BUFFER TOWER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 21 | ZSC | DI | #N/A
P-OKITM07-10-302-07-PID-4644 | TM140021 | TM1400JBS011 |  | TM140021HS013 | TM140021SV013.ZSO | TM140021SV013.GSO | OVER FLOW PUMP OUTLET TO W.W BUFFER TOWER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 21 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4644 | TM140021 | TM1400JBS011 |  | TM140021HS013 | TM140021EV013 | TM140021EV013 | OVER FLOW PUMP OUTLET TO W.W BUFFER TOWER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 21 | EV | DO | #N/A
P-OKITM07-10-302-07-PID-4644 | TM140022 | TM1400JBA005 |  | TM140022PC001 | TM140022PT001 | TM140022PT001.MV | SP SEALING WATER PUMP 3 OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1 |  |  | 1400 | 22 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4644 | TM140022 | TM1400JBA005 |  | TM140022PI002 | TM140022PT002 | TM140022PT002.MV | SP SEALING WATER FILTER INLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1 |  |  | 1400 | 22 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4644 | TM140022 | TM1400JBA005 |  | TM140022PI003 | TM140022PT003 | TM140022PT003.MV | SP SEALING WATER FILTER OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 10 | Bar.g | [19 empty] | 1 |  |  | 1400 | 22 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4644 | TM140022 |  |  | TM140022PDI004 | TM140022PDX004 | TM140022PDX004.SOF | SP SEALING WATER FILTER DIFFERENTIAL PRESSURE | PD | DCS software function | DCS | DCS |  | Software function |  |  |  | 0 | 2 | Bar.g | [19 empty] | B |  |  | 1400 | 22 | PDX |  | Bar.g
P-OKITM07-10-302-07-PID-4644 | TM140022 | TM1400CP01 |  | TM140022XS005 | TM140022S1.005 | TM140022S1.005 | SP SEALING WATER FILTER LOCAL PANEL | S1 | Differential Pressure High alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140022 | TM1400CP01 |  | TM140022XS005 | TM140022S2.005 | TM140022S2.005 | SP SEALING WATER FILTER LOCAL PANEL | S2 | Flush alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140022 | TM1400CP01 |  | TM140022XS005 | TM140022S3.005 | TM140022S3.005 | SP SEALING WATER FILTER LOCAL PANEL | S3 | Power Failure alarm | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140022 | TM1400JBA005 |  | TM140022PC011 | TM140022PT011 | TM140022PT011.MV | MAKE UP FRESH WATER PUMP 3 OUTLET PRESSURE | PT | Pressure Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 6 | Bar.g | [19 empty] | 1 |  |  | 1400 | 22 | PT | AI | bar,kPa,g/kg,bar(g),Bar.g
P-OKITM07-10-302-07-PID-4644 | TM140022 |  |  | TM140022FI012 | TM140022FE012 |  | MAKE UP FRESH WATER PUMP 3 OUTLET TO SP FLOW | FE | Magnetic Flow Sensor | Field | [31 empty] | 1400 | 22 | FE |  | #N/A
P-OKITM07-10-302-07-PID-4644 | TM140022 | TM1400JBA002 |  | TM140022FI012 | TM140022FT012 | TM140022FT012.MV | MAKE UP FRESH WATER PUMP 3 OUTLET TO SP FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 0 | 3600 | l/min | [19 empty] | 1 |  |  | 1400 | 22 | FT | AI | l/min,kg/h,mc/h,t / hr,m3/hr
P-OKITM07-10-302-07-PID-4644 | TM140022 |  |  | TM140022FI013 | TM140022FI013 | TM140022FI013.SOF | FRESH WATER TOTAL FLOW CALCULATED | FI | DCS software function | DCS | DCS |  | Software function | [28 empty] | 1400 | 22 | FI |  | #N/A
| FIBRE CATCHER | [43 empty] | #N/A | #N/A
P-OKITM07-10-310-07-PID-4881 | TM140021 | TM1400JBA006 |  | TM140021LC101 | TM140021LT101 | TM140021LT101.MV | FIBER FILTER LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 4000 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1 |  |  | 1400 | 21 | LT | AI | %,mm
P-OKITM07-10-310-07-PID-4881 | TM140021 | TM1400JBA006 | TM1400ASD007 | TM140021HC103 | TM140021HV103 | TM140021HV103.OUT | SHOWER WATER TO FIBER FILTER CV SETPOINT | HV | Control Valve | Field | DCS | AO | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 100 | % | [19 empty] | 1 |  |  | 1400 | 21 | HV | AO | %
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021HS104 | TM140021SV104 | TM140021SV104 | SUPER CLEAR WW PUMP TO FIBER FILTER ON/OFF VALVE | SV | On/Off Valve | Field | [28 empty] | B |  |  | 1400 | 21 | SV | DO | #N/A
P-OKITM07-10-310-07-PID-4881 | TM140021 | TM1400JBS012 |  | TM140021HS104 | TM140021SV104.ZSC | TM140021SV104.GSC | SUPER CLEAR WW PUMP TO FIBER FILTER ON/OFF VALVE CLOSED | ZSC | Limit Switch (Close) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Closed | Closed | [10 empty] | 1 |  |  | 1400 | 21 | ZSC | DI | #N/A
P-OKITM07-10-310-07-PID-4881 | TM140021 | TM1400JBS012 |  | TM140021HS104 | TM140021SV104.ZSO | TM140021SV104.GSO | SUPER CLEAR WW PUMP TO FIBER FILTER ON/OFF VALVE OPENED | ZSO | Limit Switch (Open) | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Opened | Opened | [10 empty] | 1 |  |  | 1400 | 21 | ZSO | DI | #N/A
P-OKITM07-10-302-07-PID-4644 | TM140021 | TM1400JBS012 |  | TM140021HS104 | TM140021EV104 | TM140021EV104 | SUPER CLEAR WW PUMP TO FIBER FILTER ON/OFF VALVE SOV CMD OPEN | EV | Solenoid Valve | Field | DCS | DO | Dry Contact | 24 VDC Loop | 2 | RR | [10 empty] | Not Open | Open | [10 empty] | 1 |  |  | 1400 | 21 | EV | DO | #N/A
P-OKITM07-10-310-07-PID-4881 | TM140021 | TM1400JBA006 |  | TM140021LC111 | TM140021LT111 | TM140021LT111.MV | SUPER CLEAR WHITE WATER TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3800 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1 |  |  | 1400 | 21 | LT | AI | %,mm
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021FI112 | TM140021FE112 |  | SUPER CLEAR WW PUMP TO ETP FLOW | FE | Magnetic Flow Sensor | Field | [31 empty] | 1400 | 21 | FE |  | #N/A
P-OKITM07-10-310-07-PID-4881 | TM140021 | TM1400JBA006 |  | TM140021FI112 | TM140021FT112 | TM140021FT112.MV | SUPER CLEAR WW PUMP TO ETP FLOW | FT | Magnetic Flow Transmitter | Field | DCS | AI | 4-20 mA HART | 230VAC | 2+3 | RR | 0 | 10000 | l/min | [19 empty] | 1 |  |  | 1400 | 21 | FT | AI | l/min,kg/h,mc/h,t / hr,m3/hr
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021AI113 | TM140021AE113 |  | SUPER CLEAR WW PUMP TO ETP PH | AE | pH Sensor | Field | [31 empty] | 1400 | 21 | AE |  | #N/A
P-OKITM07-10-310-07-PID-4881 | TM140021 | TM1400JBA006 |  | TM140021AI113 | TM140021AT113 | TM140021AT113.MV | SUPER CLEAR WW PUMP TO ETP PH | AT | pH Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 14 | Ph | [19 empty] | 1 |  |  | 1400 | 21 | AT | AI | Ph,ml CSF
P-OKITM07-10-310-07-PID-4881 | TM140021 | TM1400JBA006 |  | TM140021LI121 | TM140021LT121 | TM140021LT121.MV | CLOUDY WHITE WATER TANK LEVEL | LT | DP Level Transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 3500 | mm |  | 20% | 30% |  | 90% | 95% | [13 empty] | 1 |  |  | 1400 | 21 | LT | AI | %,mm
P-OKITM07-10-310-07-PID-4881 | TM140021 | TM1400JBA001 |  | TM140021FI131 | TM140021FT131 | TM140021FT131.MV | WASTE WATER FROM SP2 FLOW | FT | Open channel flow transmitter | Field | DCS | AI | 4-20 mA HART | 24 VDC Loop | 2 | RR | 0 | 250 | m3/hr | [22 empty] | 1400 | 21 | FT | AI | l/min,kg/h,mc/h,t / hr,m3/hr
| HVAC | [43 empty] | #N/A | #N/A
P-OKITM07-10-302-08-FLD-4641 | TM140000 | NA |  | TM140000PDS001 | TM140000PDS001 | TM140000PDS001.L | SP2 MCC ROOM AIR FAN FILTER 1 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 |  |  | 1400 | 0 | PDS | DI | #N/A
P-OKITM07-10-302-08-FLD-4641 | TM140000 | NA |  | TM140000PDS002 | TM140000PDS002 | TM140000PDS002.L | SP2 MCC ROOM AIR FAN FILTER 2 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 |  |  | 1400 | 0 | PDS | DI | #N/A
P-OKITM07-10-302-08-FLD-4641 | TM140000 | NA |  | TM140000PDS003 | TM140000PDS003 | TM140000PDS003.L | SP2 MCC ROOM AIR FAN FILTER 3 DIFFERENTIAL PRESSURE | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 |  |  | 1400 | 0 | PDS | DI | #N/A
P-OKITM07-10-302-08-FLD-4641 | TM140000 | NA |  | TM140000PDS004 | TM140000PDS004 | TM140000PDS004.L | SP2 MCC ROOM AIR FAN FILTER 4 DIFFERENTIAL PRESSURE (MAU1) | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 |  |  | 1400 | 0 | PDS | DI | #N/A
P-OKITM07-10-302-08-FLD-4641 | TM140000 | NA |  | TM140000PDS005 | TM140000PDS005 | TM140000PDS005.L | SP2 MCC ROOM AIR FAN FILTER 4 DIFFERENTIAL PRESSURE (MAU2) | PDS | Diff. Pressure Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 |  |  | 1400 | 0 | PDS | DI | #N/A
P-OKITM07-10-302-08-FLD-4641 | TM140000 | NA |  | TM140000XS006 | TM140000XS006 | TM140000XS006 | SP2 MCC ROOM AC1 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 |  |  | 1400 | 0 | XS | DI | #N/A
P-OKITM07-10-302-08-FLD-4641 | TM140000 | NA |  | TM140000XS007 | TM140000XS007 | TM140000XS007 | SP2 MCC ROOM AC2 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 |  |  | 1400 | 0 | XS | DI | #N/A
P-OKITM07-10-302-08-FLD-4641 | TM140000 | NA |  | TM140000XS008 | TM140000XS008 | TM140000XS008 | SP2 MCC ROOM AC3 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 |  |  | 1400 | 0 | XS | DI | #N/A
P-OKITM07-10-302-08-FLD-4641 | TM140000 | NA |  | TM140000XS009 | TM140000XS009 | TM140000XS009 | SP2 MCC ROOM AC4 ON-OFF SWITCH | XS | Limit Switch | Field | DCS | DI | Dry Contact | 24 VDC Loop | 2 | RR | [22 empty] | 3 |  |  | 1400 | 0 | XS | DI | #N/A
P-OKITM07-10-302-08-FLD-4641 | TM140000 | NA |  | TM140000II010 | TM140000IT010 | TM140000IT010.MV | SP2 MCC ROOM AC PANEL POWER METER DATA | IT | Ammeter Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | [22 empty] | 3 |  |  | 1400 | 0 | IT | AI
P-OKITM07-10-302-08-FLD-4641 | TM140000 | NA |  | TM140000TI011 | TM140000TT011 | TM140000TT011.MV | SP2 MV/SW GEAR ROOM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 0 | 50 | ˚C | [19 empty] | 3 |  |  | 1400 | 0 | TT | AI | °C,℃,˚C
P-OKITM07-10-302-08-FLD-4641 | TM140000 | NA |  | TM140000MI012 | TM140000MT012 | TM140000MT012.MV | SP2 MV/SW GEAR ROOM HUMIDITY | MT | Humidity Transmitter(Integrated In TT) | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 40 | 60 | % | [19 empty] | 3 |  |  | 1400 | 0 | MT | AI | %,Pa,g/kg
P-OKITM07-10-302-08-FLD-4641 | TM140000 | NA |  | TM140000TI013 | TM140000TT013 | TM140000TT013.MV | SP2 MCC ROOM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 0 | 50 | ˚C | [19 empty] | 3 |  |  | 1400 | 0 | TT | AI | °C,℃,˚C
P-OKITM07-10-302-08-FLD-4641 | TM140000 | NA |  | TM140000MI014 | TM140000MT014 | TM140000MT014.MV | SP2 MCC ROOM HUMIDITY | MT | Humidity Transmitter(Integrated In TT) | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 40 | 60 | % | [19 empty] | 3 |  |  | 1400 | 0 | MT | AI | %,Pa,g/kg
P-OKITM07-10-302-08-FLD-4641 | TM140000 | NA |  | TM140000TI015 | TM140000TT015 | TM140000TT015.MV | SP2 RACK ROOM TEMPERATURE | TT | Temperature Transmitter | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 0 | 50 | ˚C | [19 empty] | 3 |  |  | 1400 | 0 | TT | AI | °C,℃,˚C
P-OKITM07-10-302-08-FLD-4641 | TM140000 | NA |  | TM140000MI016 | TM140000MT016 | TM140000MT016.MV | SP2 RACK ROOM HUMIDITY | MT | Humidity Transmitter(Integrated In TT) | Field | DCS | AI | 4-20 mA | 24 VDC Loop | 2 | RR | 40 | 60 | % | [19 empty] | 3 |  |  | 1400 | 0 | MT | AI | %,Pa,g/kg

## SP2 exchange Communication List
PMT: | [5 empty] | Design Institute: |  |  | Project No. | P-OKITM07-10 | [6 empty] | EXCHANGE COMMUNICTION LIST
[9 empty] | Project Name | DETAIL ENGINEERING FOR 4(FOUR) UNITS TISSUE MACHINE
[9 empty] | Doc. No. | P-OKITM07-10-302-06-LST-4645 | [7 empty] | Abbreviations
Owner: | [8 empty] | Rev. No. | 7 |  |  | Prep'd by | Dengzuijie |  |  |  | EER Electronic Equipment Room |  |  |  | SQRT Square Root
[9 empty] | Purpose | Final |  |  | Chk'd by | Chengjianguo |  |  |  | CCR Control Center Room
[9 empty] | Date | 30,8,2021 |  |  | Appv'd by | LiXiangdong |  |  |  | ESP Electrostatic Precipitator
P&ID No. | Area | JB No. | Motor Tag reference | Loop No. | Tag No. | System Tag No. | Service Description | Signal Tag | Instrument Type | Location | System | IO Type | Signal |  |  | IO Loc. | PV LO | PV HI | Eng. Unit | Alarm | [6 empty] | State "0" | State "1" | CV Fail Action | CV Ctrl Action | PV CHAR | From |  | Cable |  |  | To |  | Rev. | Supply | Remarks
[13 empty] | Type | Power | Wire |  |  |  |  | LLL | LL | L | Nor. | H | HH | HHH | [5 empty] | JB/Panel No. | TB | Cable Number | Cable Type | Cable Order | Cabinet No. | TB |  | By
LBKP Wet Line
P-OKITM07-10-302-07-PID-4641 | TM140012 |  | TM140012U001M1 | TM140012SC455 | TM140012SX455 | TM140012SX455.PRO | LBKP 2 INTERMEDIATE TOWER PUMP 1 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4641 | TM140012 |  | TM140012U002M1 | TM140012SC465 | TM140012SX465 | TM140012SX465.PRO | LBKP 2 INTERMEDIATE TOWER PUMP 2 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4641 | TM140012 |  | TM140012U003M1 | TM140012SC475 | TM140012SX475 | TM140012SX475.PRO | LBKP 2 INTERMEDIATE TOWER PUMP 3 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4641 | TM140012 |  | TM140012U004M1 | TM140012SC485 | TM140012SX485 | TM140012SX485.PRO | LBKP 2 INTERMEDIATE TOWER PUMP 4 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
Broke Line
P-OKITM07-10-302-07-PID-4642 | TM140017 |  | TM140017U001M1 | TM140017SC455 | TM140017SX455 | TM140017SX455.PRO | BROKE TOWER PUMP 1 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4642 | TM140017 |  | TM140017U002M1 | TM140017SC465 | TM140017SX465 | TM140017SX465.PRO | BROKE TOWER PUMP 2 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4642 | TM140017 |  | TM140017U003M1 | TM140017SC475 | TM140017SX475 | TM140017SX475.PRO | BROKE TOWER PUMP 3 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4642 | TM140017 |  | TM140017U004M1 | TM140017SC485 | TM140017SX485 | TM140017SX485.PRO | BROKE TOWER PUMP 4 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
NBKP 3# Line
P-OKITM07-10-302-07-PID-4643 | TM140011 |  | TM140011U011M1 | TM140011SC205 | TM140011SX205 | TM140011SX205.PRO | NBKP #1 REFINED TOWER PUMP 4 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4643 | TM140011 |  | TM140011U012M1 | TM140011SC215 | TM140011SX215 | TM140011SX215.PRO | NBKP #2 REFINED TOWER PUMP 4 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4643 | TM140011 |  | TM140011M001M1 | TM140011SC005 | TM140011SX005 | TM140011SX005.PRO | NBKP #3 PULPER AGITATOR SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC
P-OKITM07-10-302-07-PID-4643 | TM140011 |  | TM140011U002M1 | TM140011SC012 | TM140011SX012 | TM140011SX012.PRO | NBKP #3 DUMP TOWER PUMP VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4643 | TM140011 |  | TM140011C001M1 | TM140011SC042 | TM140011SX042 | TM140011SX042.PRO | BALE RECIEVING CONVEYOR VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4643 | TM140011 |  | TM140011C002M1 | TM140011SC043 | TM140011SX043 | TM140011SX043.PRO | BELT CONVEYOR VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4643 | TM140011 |  | TM140011C003M1 | TM140011SC046 | TM140011SX046 | TM140011SX046.PRO | FEEDING CONVEYOR VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4643 | TM140011 |  | TM140011C004M1 | TM140011SC074 | TM140011SX074 | TM1400111CP01 | CHAIN CONVEYOR VFC SETPOINT |  | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4643 | TM140011 |  | TM140011M005M2 | TM140011EC111 | TM140011SX111 | TM140011SX111.PRO | NBKP #3 REFINER #1 POWER VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC
P-OKITM07-10-302-07-PID-4643 | TM140011 |  | TM140011M006M2 | TM140011EC161 | TM140011SX161 | TM140011SX161.PRO | NBKP #3 REFINER #2 POWER VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC
P-OKITM07-10-302-07-PID-4643 | TM140011 |  | TM140011U003M1 | TM140011SC445 | TM140011SX445 | TM140011SX445.PRO | NBKP #3 REFINER TOWER #1 PUMP 1 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4643 | TM140011 |  | TM140011U004M1 | TM140011SC455 | TM140011SX455 | TM140011SX455.PRO | NBKP #3 REFINER TOWER #1 PUMP 2 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4643 | TM140011 |  | TM140011U005M1 | TM140011SC465 | TM140011SX465 | TM140011SX465.PRO | NBKP #3 REFINER TOWER #1 PUMP 3 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4643 | TM140011 |  | TM140011U006M1 | TM140011SC475 | TM140011SX475 | TM140011SX475.PRO | NBKP #3 REFINER TOWER #1 PUMP 4 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4643 | TM140011 |  | TM140011U007M1 | TM140011SC545 | TM140011SX545 | TM140011SX545.PRO | NBKP #3 REFINER TOWER #2 PUMP 1 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4643 | TM140011 |  | TM140011U008M1 | TM140011SC555 | TM140011SX555 | TM140011SX555.PRO | NBKP #3 REFINER TOWER #2 PUMP 2 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4643 | TM140011 |  | TM140011U009M1 | TM140011SC565 | TM140011SX565 | TM140011SX565.PRO | NBKP #3 REFINER TOWER #2 PUMP 3 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4643 | TM140011 |  | TM140011U00610M1 | TM140011SC575 | TM140011SX575 | TM140011SX575.PRO | NBKP #3 REFINER TOWER #2 PUMP 4 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
WHITE WATER AND FRESH WATER
P-OKITM07-10-302-07-PID-4644 | TM140021 |  | TM140021U001M1 | TM140021SC009 | TM140021SX009 | TM140021SX009.PRO | OVER FLOW PUMP VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4644 | TM140021 |  | TM140021U002M1 | TM140021SC008 | TM140021SX008 | TM140021SX008.PRO | PULPER W.W PUMP VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4644 | TM140021 |  | TM140021U003M1 | TM140021SC010 | TM140021SX010 | TM140021SX010.PRO | LBKP & NBKP CRC & FLUSHING PUMP1 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4644 | TM140021 |  | TM140021U004M1 | TM140021SC011 | TM140021SX011 | TM140021SX011.PRO | LBKP & NBKP CRC & FLUSHING PUMP2 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4644 | TM140022 |  | TM140022U001M1 | TM140022SC007 | TM140022SX007 | TM140022SX007.PRO | SP SEALING WATER PUMP 3 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-302-07-PID-4644 | TM140022 |  | TM140022U002M1 | TM140022SC015 | TM140022SX015 | TM140022SX015.PRO | MAKE UP FRESH WATER PUMP 3 VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
FIBRE CATCHER
P-OKITM07-10-310-07-PID-4881 | TM140021 |  | TM140021M101M1 | TM140021SC102 | TM140021SX102 | TM140021SX102.PRO | FIBRE FILTER MAIN MOTOR SPEED VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC
P-OKITM07-10-310-07-PID-4881 | TM140021 |  | TM140021U101M1 | TM140021SC115 | TM140021SX115 | TM140021SX115.PRO | SUPER CLEAR WW PUMP1 TO ETP VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
P-OKITM07-10-310-07-PID-4881 | TM140021 |  | TM140021U102M1 | TM140021SC116 | TM140021SX116 | TM140021SX116.PRO | SUPER CLEAR WW PUMP2 TO ETP VFC SETPOINT | SX | Variable frequency controller | MCC | DCS | AO | Profibus DP |  |  | MCC | [22 empty] | B
Motor IO List Except SC
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012A001M1 | TM140012A001M1_CURR | DCS | LBKP INTERMEDIATE AGITATOR |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012A001M1 | TM140012A001M1_RF | DCS | LBKP INTERMEDIATE AGITATOR |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012A001M1 | TM140012A001M1_RY | DCS | LBKP INTERMEDIATE AGITATOR |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012A001M1 | TM140012A001M1_STR | DCS | LBKP INTERMEDIATE AGITATOR |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012U001M1 | TM140012U001M1_CURR | DCS | LBKP INTERMEDIATE TOWER PUMP1 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012U001M1 | TM140012U001M1_RF | DCS | LBKP INTERMEDIATE TOWER PUMP1 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012U001M1 | TM140012U001M1_RY | DCS | LBKP INTERMEDIATE TOWER PUMP1 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012U001M1 | TM140012U001M1_STR | DCS | LBKP INTERMEDIATE TOWER PUMP1 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012U002M1 | TM140012U002M1_CURR | DCS | LBKP INTERMEDIATE TOWER PUMP2 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012U002M1 | TM140012U002M1_RF | DCS | LBKP INTERMEDIATE TOWER PUMP2 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012U002M1 | TM140012U002M1_RY | DCS | LBKP INTERMEDIATE TOWER PUMP2 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012U002M1 | TM140012U002M1_STR | DCS | LBKP INTERMEDIATE TOWER PUMP2 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012U003M1 | TM140012U003M1_CURR | DCS | LBKP INTERMEDIATE TOWER PUMP3 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012U003M1 | TM140012U003M1_RF | DCS | LBKP INTERMEDIATE TOWER PUMP3 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012U003M1 | TM140012U003M1_RY | DCS | LBKP INTERMEDIATE TOWER PUMP3 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012U003M1 | TM140012U003M1_STR | DCS | LBKP INTERMEDIATE TOWER PUMP3 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012U004M1 | TM140012U004M1_CURR | DCS | LBKP INTERMEDIATE TOWER PUMP4 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012U004M1 | TM140012U004M1_RF | DCS | LBKP INTERMEDIATE TOWER PUMP4 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012U004M1 | TM140012U004M1_RY | DCS | LBKP INTERMEDIATE TOWER PUMP4 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012U004M1 | TM140012U004M1_STR | DCS | LBKP INTERMEDIATE TOWER PUMP4 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012NE452 | TM140012NE452_RF | DCS | LBKP 2 INTERMEDIATE TOWER PUMP 1 OUTPUT CONSISTENCY |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012NE452 | TM140012NE452_RY | DCS | LBKP 2 INTERMEDIATE TOWER PUMP 1 OUTPUT CONSISTENCY |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012NE452 | TM140012NE452_STR | DCS | LBKP 2 INTERMEDIATE TOWER PUMP 1 OUTPUT CONSISTENCY |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012NE462 | TM140012NE462_RF | DCS | LBKP 2 INTERMEDIATE TOWER PUMP 2 OUTPUT CONSISTENCY |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012NE462 | TM140012NE462_RY | DCS | LBKP 2 INTERMEDIATE TOWER PUMP 2 OUTPUT CONSISTENCY |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012NE462 | TM140012NE462_STR | DCS | LBKP 2 INTERMEDIATE TOWER PUMP 2 OUTPUT CONSISTENCY |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012NE472 | TM140012NE472_RF | DCS | LBKP 2 INTERMEDIATE TOWER PUMP 3 OUTPUT CONSISTENCY |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012NE472 | TM140012NE472_RY | DCS | LBKP 2 INTERMEDIATE TOWER PUMP 3 OUTPUT CONSISTENCY |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012NE472 | TM140012NE472_STR | DCS | LBKP 2 INTERMEDIATE TOWER PUMP 3 OUTPUT CONSISTENCY |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012NE482 | TM140012NE482_RF | DCS | LBKP 2 INTERMEDIATE TOWER PUMP 4 OUTPUT CONSISTENCY |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012NE482 | TM140012NE482_RY | DCS | LBKP 2 INTERMEDIATE TOWER PUMP 4 OUTPUT CONSISTENCY |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4641 | TM140012 |  |  | TM140012NE482 | TM140012NE482_STR | DCS | LBKP 2 INTERMEDIATE TOWER PUMP 4 OUTPUT CONSISTENCY |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017A001M1 | TM140017A001M1_CURR | DCS | BROKE TOWER AGITATOR |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017A001M1 | TM140017A001M1_RF | DCS | BROKE TOWER AGITATOR |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017A001M1 | TM140017A001M1_RY | DCS | BROKE TOWER AGITATOR |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017A001M1 | TM140017A001M1_STR | DCS | BROKE TOWER AGITATOR |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017U001M1 | TM140017U001M1_CURR | DCS | BROKE TOWER PUMP1 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017U001M1 | TM140017U001M1_RF | DCS | BROKE TOWER PUMP1 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017U001M1 | TM140017U001M1_RY | DCS | BROKE TOWER PUMP1 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017U001M1 | TM140017U001M1_STR | DCS | BROKE TOWER PUMP1 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017U002M1 | TM140017U002M1_CURR | DCS | BROKE TOWER PUMP2 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017U002M1 | TM140017U002M1_RF | DCS | BROKE TOWER PUMP2 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017U002M1 | TM140017U002M1_RY | DCS | BROKE TOWER PUMP2 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017U002M1 | TM140017U002M1_STR | DCS | BROKE TOWER PUMP2 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017U003M1 | TM140017U003M1_CURR | DCS | BROKE TOWER PUMP3 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017U003M1 | TM140017U003M1_RF | DCS | BROKE TOWER PUMP3 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017U003M1 | TM140017U003M1_RY | DCS | BROKE TOWER PUMP3 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017U003M1 | TM140017U003M1_STR | DCS | BROKE TOWER PUMP3 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017U004M1 | TM140017U004M1_CURR | DCS | BROKE TOWER PUMP4 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017U004M1 | TM140017U004M1_RF | DCS | BROKE TOWER PUMP4 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017U004M1 | TM140017U004M1_RY | DCS | BROKE TOWER PUMP4 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017U004M1 | TM140017U004M1_STR | DCS | BROKE TOWER PUMP4 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017U005M1 | TM140017U005M1_CURR | DCS | BROKE TOWER PUMP5 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017U005M1 | TM140017U005M1_RF | DCS | BROKE TOWER PUMP5 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017U005M1 | TM140017U005M1_RY | DCS | BROKE TOWER PUMP5 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017U005M1 | TM140017U005M1_STR | DCS | BROKE TOWER PUMP5 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017NE452 | TM140017NE452_RF | DCS | BROKE TOWER PUMP 1 OUTPUT CONSISTENCY |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017NE452 | TM140017NE452_RY | DCS | BROKE TOWER PUMP 1 OUTPUT CONSISTENCY |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017NE452 | TM140017NE452_STR | DCS | BROKE TOWER PUMP 1 OUTPUT CONSISTENCY |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017NE462 | TM140017NE462_RF | DCS | BROKE TOWER PUMP 2 OUTPUT CONSISTENCY |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017NE462 | TM140017NE462_RY | DCS | BROKE TOWER PUMP 2 OUTPUT CONSISTENCY |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017NE462 | TM140017NE462_STR | DCS | BROKE TOWER PUMP 2 OUTPUT CONSISTENCY |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017NE472 | TM140017NE472_RF | DCS | BROKE TOWER PUMP 3 OUTPUT CONSISTENCY |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017NE472 | TM140017NE472_RY | DCS | BROKE TOWER PUMP 3 OUTPUT CONSISTENCY |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017NE472 | TM140017NE472_STR | DCS | BROKE TOWER PUMP 3 OUTPUT CONSISTENCY |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017NE482 | TM140017NE482_RF | DCS | BROKE TOWER PUMP 4 OUTPUT CONSISTENCY |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017NE482 | TM140017NE482_RY | DCS | BROKE TOWER PUMP 4 OUTPUT CONSISTENCY |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4642 | TM140017 |  |  | TM140017NE482 | TM140017NE482_STR | DCS | BROKE TOWER PUMP 4 OUTPUT CONSISTENCY |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011A001M1 | TM140011A001M1_CURR | DCS | Agitato NBKP#3 Dump Tower |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011A001M1 | TM140011A001M1_RF | DCS | Agitato NBKP#3 Dump Tower |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011A001M1 | TM140011A001M1_RY | DCS | Agitato NBKP#3 Dump Tower |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011A001M1 | TM140011A001M1_STR | DCS | Agitato NBKP#3 Dump Tower |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011A002M1 | TM140011A002M1_CURR | DCS | Agitator NBKP #3 Refined Tower #1 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011A002M1 | TM140011A002M1_RF | DCS | Agitator NBKP #3 Refined Tower #1 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011A002M1 | TM140011A002M1_RY | DCS | Agitator NBKP #3 Refined Tower #1 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011A002M1 | TM140011A002M1_STR | DCS | Agitator NBKP #3 Refined Tower #1 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011A003M1 | TM140011A003M1_CURR | DCS | Agitator NBKP #3 Refined Tower #2 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011A003M1 | TM140011A003M1_RF | DCS | Agitator NBKP #3 Refined Tower #2 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011A003M1 | TM140011A003M1_RY | DCS | Agitator NBKP #3 Refined Tower #2 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011A003M1 | TM140011A003M1_STR | DCS | Agitator NBKP #3 Refined Tower #2 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011C001M1 | TM140011C001M1_CURR | DCS | Bale Recieving Conveyor |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011C001M1 | TM140011C001M1_RF | DCS | Bale Recieving Conveyor |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011C001M1 | TM140011C001M1_RY | DCS | Bale Recieving Conveyor |  | Motor Start FWD | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011C001M1 | TM140011C001M1_STR | DCS | Bale Recieving Conveyor |  | Motor Start REV | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011C002M1 | TM140011C002M1_CURR | DCS | Belt Conveyor |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011C002M1 | TM140011C002M1_RF | DCS | Belt Conveyor |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011C002M1 | TM140011C002M1_RY | DCS | Belt Conveyor |  | Motor Start FWD | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011C002M1 | TM140011C002M1_STR | DCS | Belt Conveyor |  | Motor Start REV | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011C003M1 | TM140011C003M1_CURR | DCS | Feeding Conveyor |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011C003M1 | TM140011C003M1_RF | DCS | Feeding Conveyor |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011C003M1 | TM140011C003M1_RY | DCS | Feeding Conveyor |  | Motor Start FWD | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011C003M1 | TM140011C003M1_STR | DCS | Feeding Conveyor |  | Motor Start REV | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011C004M1 | TM140011C004M1_CURR | DCS | Chain Conveyor |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011C004M1 | TM140011C004M1_RF | DCS | Chain Conveyor |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011C004M1 | TM140011C004M1_RY | DCS | Chain Conveyor |  | Motor Start FWD | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011C004M1 | TM140011C004M1_STR | DCS | Chain Conveyor |  | Motor Start REV | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M001M1 | TM140011M001M1_CURR | DCS | NBKP #3 Pulper |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M001M1 | TM140011M001M1_RF | DCS | NBKP #3 Pulper |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M001M1 | TM140011M001M1_RY | DCS | NBKP #3 Pulper |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M001M1 | TM140011M001M1_STR | DCS | NBKP #3 Pulper |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M004M1 | TM140011M004M1_CURR | DCS | Deflaker NBKP#3 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M004M1 | TM140011M004M1_RF | DCS | Deflaker NBKP#3 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M004M1 | TM140011M004M1_RY | DCS | Deflaker NBKP#3 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M004M1 | TM140011M004M1_STR | DCS | Deflaker NBKP#3 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M005M1 | TM140011M005M1_CURR | DCS | Refiner1 NBKP#3 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M005M1 | TM140011M005M1_FLT | DCS | Refiner1 NBKP#3 |  | Fault | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M005M1 | TM140011M005M1_RY | DCS | Refiner1 NBKP#3 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M005M1 | TM140011M005M1_STR | DCS | Refiner1 NBKP#3 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M005M1 | TM140011M005M1_STP | DCS | Refiner1 NBKP#3 |  | Motor Stop | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M005M2 | TM140011M005M2_RF | DCS | Plate Adjustment Refiner 1 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5 |  | Command signal from DCS is profibus to VFD of the plate adjustment
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M005M2 | TM140011M005M2_RY | DCS | Plate Adjustment Refiner 1 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M005M2 | TM140011M005M2_STR | DCS | Plate Adjustment Refiner 1 |  | Load Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M005M2 | TM140011M005M2_STR | DCS | Plate Adjustment Refiner 1 |  | Release Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M005M2 | TM140011M005M2_FS | DCS | Plate Adjustment Refiner 1 |  | Release Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M006M1 | TM140011M006M1_CURR | DCS | Refiner 2 NBKP#3 |  | Fast Speed | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M006M1 | TM140011M006M1_FLT | DCS | Refiner 2 NBKP#3 |  | Fault | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M006M1 | TM140011M006M1_RY | DCS | Refiner 2 NBKP#3 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M006M1 | TM140011M006M1_STR | DCS | Refiner 2 NBKP#3 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M006M1 | TM140011M006M1_STP | DCS | Refiner 2 NBKP#3 |  | Motor Stop | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M006M2 | TM140011M006M2_RF | DCS | Plate Adjustment Refiner 2 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5 |  | Command signal from DCS is profibus to VFD of the plate adjustment
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M006M2 | TM140011M006M2_RY | DCS | Plate Adjustment Refiner 2 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M006M2 | TM140011M006M2_STR | DCS | Plate Adjustment Refiner 2 |  | Load Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M006M2 | TM140011M006M2_STR | DCS | Plate Adjustment Refiner 2 |  | Release Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011M005M2 | TM140011M006M2_FS | DCS | Plate Adjustment Refiner 2 |  | Release Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE202 | TM140011NE202_RF | DCS | NBKP #1 REFINED TOWER PUMP 4 OUTPUT CONSISTENCY |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE202 | TM140011NE202_RY | DCS | NBKP #1 REFINED TOWER PUMP 4 OUTPUT CONSISTENCY |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE202 | TM140011NE202_STR | DCS | NBKP #1 REFINED TOWER PUMP 4 OUTPUT CONSISTENCY |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE212 | TM140011NE212_RF | DCS | NBKP #2 REFINED TOWER PUMP 4 OUTPUT CONSISTENCY |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE212 | TM140011NE212_RY | DCS | NBKP #2 REFINED TOWER PUMP 4 OUTPUT CONSISTENCY |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE212 | TM140011NE212_STR | DCS | NBKP #2 REFINED TOWER PUMP 4 OUTPUT CONSISTENCY |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE011 | TM140011NE011_RF | DCS | Cons.Trans. After Dump Tower |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE011 | TM140011NE011_RY | DCS | Cons.Trans. After Dump Tower |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE011 | TM140011NE011_STR | DCS | Cons.Trans. After Dump Tower |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE442 | TM140011NE442_RF | DCS | Cons.Trans 1. After NBKP #3 Refined Tower #1 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE442 | TM140011NE442_RY | DCS | Cons.Trans 1. After NBKP #3 Refined Tower #1 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE442 | TM140011NE442_STR | DCS | Cons.Trans 1. After NBKP #3 Refined Tower #1 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE452 | TM140011NE452_RF | DCS | Cons.Trans 2. After NBKP #3 Refined Tower #1 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE452 | TM140011NE452_RY | DCS | Cons.Trans 2. After NBKP #3 Refined Tower #1 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE452 | TM140011NE452_STR | DCS | Cons.Trans 2. After NBKP #3 Refined Tower #1 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE462 | TM140011NE462_RF | DCS | Cons.Trans 3. After NBKP #3 Refined Tower #1 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE462 | TM140011NE462_RY | DCS | Cons.Trans 3. After NBKP #3 Refined Tower #1 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE462 | TM140011NE462_STR | DCS | Cons.Trans 3. After NBKP #3 Refined Tower #1 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE472 | TM140011NE472_RF | DCS | Cons.Trans 4. After NBKP #3 Refined Tower #1 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE472 | TM140011NE472_RY | DCS | Cons.Trans 4. After NBKP #3 Refined Tower #1 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE472 | TM140011NE472_STR | DCS | Cons.Trans 4. After NBKP #3 Refined Tower #1 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE542 | TM140011NE542_RF | DCS | Cons.Trans 1. After NBKP #3 Refined Tower #2 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE542 | TM140011NE542_RY | DCS | Cons.Trans 1. After NBKP #3 Refined Tower #2 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE542 | TM140011NE542_STR | DCS | Cons.Trans 1. After NBKP #3 Refined Tower #2 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE552 | TM140011NE552_RF | DCS | Cons.Trans 2. After NBKP #3 Refined Tower #2 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE552 | TM140011NE552_RY | DCS | Cons.Trans 2. After NBKP #3 Refined Tower #2 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE552 | TM140011NE552_STR | DCS | Cons.Trans 2. After NBKP #3 Refined Tower #2 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE562 | TM140011NE562_RF | DCS | Cons.Trans 3. After NBKP #3 Refined Tower #2 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE562 | TM140011NE562_RY | DCS | Cons.Trans 3. After NBKP #3 Refined Tower #2 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE562 | TM140011NE562_STR | DCS | Cons.Trans 3. After NBKP #3 Refined Tower #2 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE572 | TM140011NE572_RF | DCS | Cons.Trans 4. After NBKP #3 Refined Tower #2 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE572 | TM140011NE572_RY | DCS | Cons.Trans 4. After NBKP #3 Refined Tower #2 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011NE572 | TM140011NE572_STR | DCS | Cons.Trans 4. After NBKP #3 Refined Tower #2 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U001M1 | TM140011U001M1_CURR | DCS | Pump NBKP#3 Pulper Discharge |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U001M1 | TM140011U001M1_RF | DCS | Pump NBKP#3 Pulper Discharge |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U001M1 | TM140011U001M1_RY | DCS | Pump NBKP#3 Pulper Discharge |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U001M1 | TM140011U001M1_STR | DCS | Pump NBKP#3 Pulper Discharge |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U002M1 | TM140011U002M1_CURR | DCS | Pump Feed HD Cleaner |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U002M1 | TM140011U002M1_RF | DCS | Pump Feed HD Cleaner |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U002M1 | TM140011U002M1_RY | DCS | Pump Feed HD Cleaner |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U002M1 | TM140011U002M1_STR | DCS | Pump Feed HD Cleaner |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U003M1 | TM140011U003M1_CURR | DCS | Pump #1 NBKP #3 Refined Tower #1 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U003M1 | TM140011U003M1_RF | DCS | Pump #1 NBKP #3 Refined Tower #1 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U003M1 | TM140011U003M1_RY | DCS | Pump #1 NBKP #3 Refined Tower #1 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U003M1 | TM140011U003M1_STR | DCS | Pump #1 NBKP #3 Refined Tower #1 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U004M1 | TM140011U004M1_CURR | DCS | Pump #2 NBKP #3 Refined Tower #1 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U004M1 | TM140011U004M1_RF | DCS | Pump #2 NBKP #3 Refined Tower #1 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U004M1 | TM140011U004M1_RY | DCS | Pump #2 NBKP #3 Refined Tower #1 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U004M1 | TM140011U004M1_STR | DCS | Pump #2 NBKP #3 Refined Tower #1 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U005M1 | TM140011U005M1_CURR | DCS | Pump #3 NBKP #3 Refined Tower #1 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U005M1 | TM140011U005M1_RF | DCS | Pump #3 NBKP #3 Refined Tower #1 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U005M1 | TM140011U005M1_RY | DCS | Pump #3 NBKP #3 Refined Tower #1 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U005M1 | TM140011U005M1_STR | DCS | Pump #3 NBKP #3 Refined Tower #1 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U006M1 | TM140011U006M1_CURR | DCS | Pump #4 NBKP #3 Refined Tower #1 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U006M1 | TM140011U006M1_RF | DCS | Pump #4 NBKP #3 Refined Tower #1 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U006M1 | TM140011U006M1_RY | DCS | Pump #4 NBKP #3 Refined Tower #1 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U006M1 | TM140011U006M1_STR | DCS | Pump #4 NBKP #3 Refined Tower #1 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U007M1 | TM140011U007M1_CURR | DCS | Pump #1 NBKP #3 Refined Tower #2 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U007M1 | TM140011U007M1_RF | DCS | Pump #1 NBKP #3 Refined Tower #2 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U007M1 | TM140011U007M1_RY | DCS | Pump #1 NBKP #3 Refined Tower #2 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U007M1 | TM140011U007M1_STR | DCS | Pump #1 NBKP #3 Refined Tower #2 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U008M1 | TM140011U008M1_CURR | DCS | Pump #2 NBKP #3 Refined Tower #2 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U008M1 | TM140011U008M1_RF | DCS | Pump #2 NBKP #3 Refined Tower #2 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U008M1 | TM140011U008M1_RY | DCS | Pump #2 NBKP #3 Refined Tower #2 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U008M1 | TM140011U008M1_STR | DCS | Pump #2 NBKP #3 Refined Tower #2 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U009M1 | TM140011U009M1_CURR | DCS | Pump #3 NBKP #3 Refined Tower #2 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U009M1 | TM140011U009M1_RF | DCS | Pump #3 NBKP #3 Refined Tower #2 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U009M1 | TM140011U009M1_RY | DCS | Pump #3 NBKP #3 Refined Tower #2 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U009M1 | TM140011U009M1_STR | DCS | Pump #3 NBKP #3 Refined Tower #2 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U010M1 | TM140011U010M1_CURR | DCS | Pump #4 NBKP #3 Refined Tower #2 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U010M1 | TM140011U010M1_RF | DCS | Pump #4 NBKP #3 Refined Tower #2 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U010M1 | TM140011U010M1_RY | DCS | Pump #4 NBKP #3 Refined Tower #2 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U010M1 | TM140011U010M1_STR | DCS | Pump #4 NBKP #3 Refined Tower #2 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U011M1 | TM140011U011M1_CURR | DCS | NBKP #1 REFINED TOWER PUMP 4 (Located at SP1) |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U011M1 | TM140011U011M1_RF | DCS | NBKP #1 REFINED TOWER PUMP 4 (Located at SP1) |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U011M1 | TM140011U011M1_RY | DCS | NBKP #1 REFINED TOWER PUMP 4 (Located at SP1) |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U011M1 | TM140011U011M1_STR | DCS | NBKP #1 REFINED TOWER PUMP 4 (Located at SP1) |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U012M1 | TM140011U012M1_CURR | DCS | NBKP #2 REFINED TOWER PUMP 4 (Located at SP1) |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U012M1 | TM140011U012M1_RF | DCS | NBKP #2 REFINED TOWER PUMP 4 (Located at SP1) |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U012M1 | TM140011U012M1_RY | DCS | NBKP #2 REFINED TOWER PUMP 4 (Located at SP1) |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4643 | TM140011 |  |  | TM140011U012M1 | TM140011U012M1_STR | DCS | NBKP #2 REFINED TOWER PUMP 4 (Located at SP1) |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140021 |  |  | TM140021U001M1 | TM140021U001M1_CURR | DCS | OVER FLOW PUMP |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140021 |  |  | TM140021U001M1 | TM140021U001M1_RF | DCS | OVER FLOW PUMP |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140021 |  |  | TM140021U001M1 | TM140021U001M1_RY | DCS | OVER FLOW PUMP |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140021 |  |  | TM140021U001M1 | TM140021U001M1_STR | DCS | OVER FLOW PUMP |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140021 |  |  | TM140021U002M1 | TM140021U002M1_CURR | DCS | PULPER WHITE WATER PUMP |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140021 |  |  | TM140021U002M1 | TM140021U002M1_RF | DCS | PULPER WHITE WATER PUMP |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140021 |  |  | TM140021U002M1 | TM140021U002M1_RY | DCS | PULPER WHITE WATER PUMP |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140021 |  |  | TM140021U002M1 | TM140021U002M1_STR | DCS | PULPER WHITE WATER PUMP |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140021 |  |  | TM140021U003M1 | TM140021U003M1_CURR | DCS | LBKP NBKP CRC FLUSHING PUMP 1 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140021 |  |  | TM140021U003M1 | TM140021U003M1_RF | DCS | LBKP NBKP CRC FLUSHING PUMP 1 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140021 |  |  | TM140021U003M1 | TM140021U003M1_RY | DCS | LBKP NBKP CRC FLUSHING PUMP 1 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140021 |  |  | TM140021U003M1 | TM140021U003M1_STR | DCS | LBKP NBKP CRC FLUSHING PUMP 1 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140021 |  |  | TM140021U004M1 | TM140021U004M1_CURR | DCS | LBKP NBKP CRC FLUSHING PUMP 2 |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140021 |  |  | TM140021U004M1 | TM140021U004M1_RF | DCS | LBKP NBKP CRC FLUSHING PUMP 2 |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140021 |  |  | TM140021U004M1 | TM140021U004M1_RY | DCS | LBKP NBKP CRC FLUSHING PUMP 2 |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140021 |  |  | TM140021U004M1 | TM140021U004M1_STR | DCS | LBKP NBKP CRC FLUSHING PUMP 2 |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140022 |  |  | TM140022U001M1 | TM140022U001M1_CURR | DCS | SP SEALING WATER PUMP #3(Located at SP1) |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140022 |  |  | TM140022U001M1 | TM140022U001M1_RF | DCS | SP SEALING WATER PUMP #3(Located at SP1) |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140022 |  |  | TM140022U001M1 | TM140022U001M1_RY | DCS | SP SEALING WATER PUMP #3(Located at SP1) |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140022 |  |  | TM140022U001M1 | TM140022U001M1_STR | DCS | SP SEALING WATER PUMP #3(Located at SP1) |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140022 |  |  | TM140022U002M1 | TM140022U002M1_CURR | DCS | MAKE UP FRESH WATER PUMP #3 (Located at SP1) |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140022 |  |  | TM140022U002M1 | TM140022U002M1_RF | DCS | MAKE UP FRESH WATER PUMP #3 (Located at SP1) |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140022 |  |  | TM140022U002M1 | TM140022U002M1_RY | DCS | MAKE UP FRESH WATER PUMP #3 (Located at SP1) |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-302-07-PID-4644 | TM140022 |  |  | TM140022U002M1 | TM140022U002M1_STR | DCS | MAKE UP FRESH WATER PUMP #3 (Located at SP1) |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021M101M1 | TM140021M101M1_CURR | DCS | FIBRE FILTER MAIN MOTOR |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021M101M1 | TM140021M101M1_RF | DCS | FIBRE FILTER MAIN MOTOR |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021M101M1 | TM140021M101M1_RY | DCS | FIBRE FILTER MAIN MOTOR |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021M101M1 | TM140021M101M1_STR | DCS | FIBRE FILTER MAIN MOTOR |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021U101M1 | TM140021U101M1_CURR | DCS | SUPER CLEAR WW PUMP1 TO ETP |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021U101M1 | TM140021U101M1_RF | DCS | SUPER CLEAR WW PUMP1 TO ETP |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021U101M1 | TM140021U101M1_RY | DCS | SUPER CLEAR WW PUMP1 TO ETP |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021U101M1 | TM140021U101M1_STR | DCS | SUPER CLEAR WW PUMP1 TO ETP |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021U102M1 | TM140021U102M1_CURR | DCS | SUPER CLEAR WW PUMP2 TO ETP |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021U102M1 | TM140021U102M1_RF | DCS | SUPER CLEAR WW PUMP2 TO ETP |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021U102M1 | TM140021U102M1_RY | DCS | SUPER CLEAR WW PUMP2 TO ETP |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021U102M1 | TM140021U102M1_STR | DCS | SUPER CLEAR WW PUMP2 TO ETP |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021A102M1 | TM140021A102M1_CURR | DCS | FC CLOUDY WW TANK AGITATOR |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021A102M1 | TM140021A102M1_RF | DCS | FC CLOUDY WW TANK AGITATOR |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021A102M1 | TM140021A102M1_RY | DCS | FC CLOUDY WW TANK AGITATOR |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021A102M1 | TM140021A102M1_STR | DCS | FC CLOUDY WW TANK AGITATOR |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021U103M1 | TM140021U103M1_CURR | DCS | FC CLOUDY WW TANK PUMP |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021U103M1 | TM140021U103M1_RF | DCS | FC CLOUDY WW TANK PUMP |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021U103M1 | TM140021U103M1_RY | DCS | FC CLOUDY WW TANK PUMP |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021U103M1 | TM140021U103M1_STR | DCS | FC CLOUDY WW TANK PUMP |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021M104M1 | TM140021M104M1_CURR | DCS | DECONTAMINATOR |  | Actual Current | MCC | DCS | AI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021M104M1 | TM140021M104M1_RF | DCS | DECONTAMINATOR |  | Run = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021M104M1 | TM140021M104M1_RY | DCS | DECONTAMINATOR |  | Ready = 1 | MCC | DCS | DI | Profibus DP |  |  | MCC | [22 empty] | 5
P-OKITM07-10-310-07-PID-4881 | TM140021 |  |  | TM140021M104M1 | TM140021M104M1_STR | DCS | DECONTAMINATOR |  | Motor Start | MCC | DCS | DO | Profibus DP |  |  | MCC | [22 empty] | 5

## Sheet3
TM140011A001M1 | M | MCC | TM140011A001M1_CURR | Agitato NBKP#3 Dump Tower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011A001M1_CURR | AI | TRUE
TM140011A001M1 | M | MCC | TM140011A001M1_RF | Agitato NBKP#3 Dump Tower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011A001M1_RF | DI | TRUE
TM140011A001M1 | M | MCC | TM140011A001M1_RY | Agitato NBKP#3 Dump Tower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011A001M1_RY | DI | TRUE
TM140011A001M1 | M | MCC | TM140011A001M1_STR | Agitato NBKP#3 Dump Tower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011A001M1_STR | #N/A | #N/A
TM140011A002M1 | M | MCC | TM140011A002M1_CURR | Agitator NBKP #3 Refined Tower #1 | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011A002M1_CURR | AI | TRUE
TM140011A002M1 | M | MCC | TM140011A002M1_RF | Agitator NBKP #3 Refined Tower #1 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011A002M1_RF | DI | TRUE
TM140011A002M1 | M | MCC | TM140011A002M1_RY | Agitator NBKP #3 Refined Tower #1 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011A002M1_RY | DI | TRUE
TM140011A002M1 | M | MCC | TM140011A002M1_STR | Agitator NBKP #3 Refined Tower #1 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011A002M1_STR | #N/A | #N/A
TM140011A003M1 | M | MCC | TM140011A003M1_CURR | Agitator NBKP #3 Refined Tower #2 | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011A003M1_CURR | AI | TRUE
TM140011A003M1 | M | MCC | TM140011A003M1_RF | Agitator NBKP #3 Refined Tower #2 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011A003M1_RF | DI | TRUE
TM140011A003M1 | M | MCC | TM140011A003M1_RY | Agitator NBKP #3 Refined Tower #2 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011A003M1_RY | DI | TRUE
TM140011A003M1 | M | MCC | TM140011A003M1_STR | Agitator NBKP #3 Refined Tower #2 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011A003M1_STR | #N/A | #N/A
TM140011C001M1 | M | MCC | TM140011C001M1_CURR | Bale Recieving Conveyor | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011C001M1_CURR | AI | TRUE
TM140011C001M1 | M | MCC | TM140011C001M1_RY | Bale Recieving Conveyor | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011C001M1_RY | DI | TRUE
TM140011C001M1 | M | MCC | TM140011C001M1_STR | Bale Recieving Conveyor | K11 | DCS | Motor Start FWD |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011C001M1_STR | #N/A | #N/A
TM140011C001M1 | M | MCC | TM140011C001M1_STR | Bale Recieving Conveyor | K12 | DCS | Motor Start REV |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011C001M1_STR | DO | TRUE
TM140011C002M1 | M | MCC | TM140011C002M1_CURR | Belt Conveyor | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011C002M1_CURR | AI | TRUE
TM140011C002M1 | M | MCC | TM140011C002M1_RY | Belt Conveyor | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011C002M1_RY | DI | TRUE
TM140011C002M1 | M | MCC | TM140011C002M1_STR | Belt Conveyor | K11 | DCS | Motor Start FWD |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011C002M1_STR | #N/A | #N/A
TM140011C002M1 | M | MCC | TM140011C002M1_STR | Belt Conveyor | K12 | DCS | Motor Start REV |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011C002M1_STR | DO | TRUE
TM140011C003M1 | M | MCC | TM140011C003M1_CURR | Feeding Conveyor | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011C003M1_CURR | AI | TRUE
TM140011C003M1 | M | MCC | TM140011C003M1_RY | Feeding Conveyor | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011C003M1_RY | DI | TRUE
TM140011C003M1 | M | MCC | TM140011C003M1_STR | Feeding Conveyor | K11 | DCS | Motor Start FWD |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011C003M1_STR | #N/A | #N/A
TM140011C003M1 | M | MCC | TM140011C003M1_STR | Feeding Conveyor | K12 | DCS | Motor Start REV |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011C003M1_STR | DO | TRUE
TM140011C004M1 | M | MCC | TM140011C004M1_CURR | Chain Conveyor | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011C004M1_CURR | AI | TRUE
TM140011C004M1 | M | MCC | TM140011C004M1_RY | Chain Conveyor | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011C004M1_RY | DI | TRUE
TM140011C004M1 | M | MCC | TM140011C004M1_STR | Chain Conveyor | K11 | DCS | Motor Start FWD |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011C004M1_STR | #N/A | #N/A
TM140011C004M1 | M | MCC | TM140011C004M1_STR | Chain Conveyor | K12 | DCS | Motor Start REV |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011C004M1_STR | DO | TRUE
TM140011M001M1 | M | MCC | TM140011M001M1_CURR | NBKP #3 Pulper | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011M001M1_CURR | AI | TRUE
TM140011M001M1 | M | MCC | TM140011M001M1_RF | NBKP #3 Pulper | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011M001M1_RF | DI | TRUE
TM140011M001M1 | M | MCC | TM140011M001M1_RY | NBKP #3 Pulper | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011M001M1_RY | DI | TRUE
TM140011M001M1 | M | MCC | TM140011M001M1_STR | NBKP #3 Pulper | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011M001M1_STR | #N/A | #N/A
TM140011M004M1 | M | MCC | TM140011M004M1_CURR | Deflaker NBKP#3 | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011M004M1_CURR | AI | TRUE
TM140011M004M1 | M | MCC | TM140011M004M1_RF | Deflaker NBKP#3 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011M004M1_RF | DI | TRUE
TM140011M004M1 | M | MCC | TM140011M004M1_RY | Deflaker NBKP#3 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011M004M1_RY | DI | TRUE
TM140011M004M1 | M | MCC | TM140011M004M1_STR | Deflaker NBKP#3 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011M004M1_STR | #N/A | #N/A
TM140011M005M1 | M | MCC | TM140011M005M1_CURR | Refiner1 NBKP#3 | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011M005M1_CURR | AI | TRUE
TM140011M005M1 | M | MCC | TM140011M005M1_FLT | Refiner1 NBKP#3 | K4 | DCS | Fault |  |  |  | Profibus |  |  | BUS | DI |  | _FLT | TM140011M005M1_FLT | DI | TRUE
TM140011M005M1 | M | MCC | TM140011M005M1_RY | Refiner1 NBKP#3 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011M005M1_RY | DI | TRUE
TM140011M005M1 | M | MCC | TM140011M005M1_STR | Refiner1 NBKP#3 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011M005M1_STR | #N/A | #N/A
TM140011M005M1 | M | MCC | TM140011M005M1_STP | Refiner1 NBKP#3 | K12 | DCS | Motor Stop |  |  |  | Profibus |  |  | BUS | DO |  | _STP | TM140011M005M1_STP | DO | TRUE
TM140011M005M2 | M | MCC | TM140011M005M2_RF | Plate Adjustment Refiner 1 | K1 | DCS | Run = 1 |  |  |  | Dry Contact | NO | 24 VDC | HW | DI |  | _RF | TM140011M005M2_RF | DI | TRUE
TM140011M005M2 | M | MCC | TM140011M005M2_RY | Plate Adjustment Refiner 1 | K5 | DCS | Ready = 1 |  |  |  | Dry Contact | NO | 24 VDC | HW | DI |  | _RY | TM140011M005M2_RY | DI | TRUE
TM140011M005M2 | M | MCC | TM140011M005M2_STR | Plate Adjustment Refiner 1 | K11 | DCS | Load Start |  |  |  | Dry Contact | NO | 24 VDC | HW | DO |  | _STR | TM140011M005M2_STR | #N/A | #N/A
TM140011M005M2 | M | MCC | TM140011M005M2_STR | Plate Adjustment Refiner 1 | K12 | DCS | Release Start |  |  |  | Dry Contact | NO | 24 VDC | HW | DO |  | _STR | TM140011M005M2_STR | DO | TRUE
TM140011M006M1 | M | MCC | TM140011M006M1_CURR | Refiner 2 NBKP#3 | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011M006M1_CURR | AI | TRUE
TM140011M006M1 | M | MCC | TM140011M006M1_FLT | Refiner 2 NBKP#3 | K4 | DCS | Fault |  |  |  | Profibus |  |  | BUS | DI |  | _FLT | TM140011M006M1_FLT | DI | TRUE
TM140011M006M1 | M | MCC | TM140011M006M1_RY | Refiner 2 NBKP#3 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011M006M1_RY | DI | TRUE
TM140011M006M1 | M | MCC | TM140011M006M1_STR | Refiner 2 NBKP#3 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011M006M1_STR | #N/A | #N/A
TM140011M006M1 | M | MCC | TM140011M006M1_STP | Refiner 2 NBKP#3 | K12 | DCS | Motor Stop |  |  |  | Profibus |  |  | BUS | DO |  | _STP | TM140011M006M1_STP | DO | TRUE
TM140011M006M2 | M | MCC | TM140011M006M2_RF | Plate Adjustment Refiner 2 | K1 | DCS | Run = 1 |  |  |  | Dry Contact | NO | 24 VDC | HW | DI |  | _RF | TM140011M006M2_RF | DI | TRUE
TM140011M006M2 | M | MCC | TM140011M006M2_RY | Plate Adjustment Refiner 2 | K5 | DCS | Ready = 1 |  |  |  | Dry Contact | NO | 24 VDC | HW | DI |  | _RY | TM140011M006M2_RY | DI | TRUE
TM140011M006M2 | M | MCC | TM140011M006M2_STR | Plate Adjustment Refiner 2 | K11 | DCS | Load Start |  |  |  | Dry Contact | NO | 24 VDC | HW | DO |  | _STR | TM140011M006M2_STR | #N/A | #N/A
TM140011M006M2 | M | MCC | TM140011M006M2_STR | Plate Adjustment Refiner 2 | K12 | DCS | Release Start |  |  |  | Dry Contact | NO | 24 VDC | HW | DO |  | _STR | TM140011M006M2_STR | DO | TRUE
TM140011NE011 | M | MCC | TM140011NE011_RF | Cons.Trans. After Dump Tower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011NE011_RF | DI | TRUE
TM140011NE011 | M | MCC | TM140011NE011_RY | Cons.Trans. After Dump Tower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011NE011_RY | DI | TRUE
TM140011NE011 | M | MCC | TM140011NE011_STR | Cons.Trans. After Dump Tower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011NE011_STR | #N/A | #N/A
TM140011NE442 | M | MCC | TM140011NE442_RF | Cons.Trans 1. After NBKP #3 Refined Tower #1 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011NE442_RF | DI | TRUE
TM140011NE442 | M | MCC | TM140011NE442_RY | Cons.Trans 1. After NBKP #3 Refined Tower #1 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011NE442_RY | DI | TRUE
TM140011NE442 | M | MCC | TM140011NE442_STR | Cons.Trans 1. After NBKP #3 Refined Tower #1 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011NE442_STR | #N/A | #N/A
TM140011NE452 | M | MCC | TM140011NE452_RF | Cons.Trans 2. After NBKP #3 Refined Tower #1 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011NE452_RF | DI | TRUE
TM140011NE452 | M | MCC | TM140011NE452_RY | Cons.Trans 2. After NBKP #3 Refined Tower #1 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011NE452_RY | DI | TRUE
TM140011NE452 | M | MCC | TM140011NE452_STR | Cons.Trans 2. After NBKP #3 Refined Tower #1 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011NE452_STR | #N/A | #N/A
TM140011NE462 | M | MCC | TM140011NE462_RF | Cons.Trans 3. After NBKP #3 Refined Tower #1 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011NE462_RF | DI | TRUE
TM140011NE462 | M | MCC | TM140011NE462_RY | Cons.Trans 3. After NBKP #3 Refined Tower #1 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011NE462_RY | DI | TRUE
TM140011NE462 | M | MCC | TM140011NE462_STR | Cons.Trans 3. After NBKP #3 Refined Tower #1 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011NE462_STR | #N/A | #N/A
TM140011NE472 | M | MCC | TM140011NE472_RF | Cons.Trans 4. After NBKP #3 Refined Tower #1 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011NE472_RF | DI | TRUE
TM140011NE472 | M | MCC | TM140011NE472_RY | Cons.Trans 4. After NBKP #3 Refined Tower #1 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011NE472_RY | DI | TRUE
TM140011NE472 | M | MCC | TM140011NE472_STR | Cons.Trans 4. After NBKP #3 Refined Tower #1 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011NE472_STR | #N/A | #N/A
TM140011NE542 | M | MCC | TM140011NE542_RF | Cons.Trans 1. After NBKP #3 Refined Tower #2 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011NE542_RF | DI | TRUE
TM140011NE542 | M | MCC | TM140011NE542_RY | Cons.Trans 1. After NBKP #3 Refined Tower #2 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011NE542_RY | DI | TRUE
TM140011NE542 | M | MCC | TM140011NE542_STR | Cons.Trans 1. After NBKP #3 Refined Tower #2 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011NE542_STR | #N/A | #N/A
TM140011NE552 | M | MCC | TM140011NE552_RF | Cons.Trans 2. After NBKP #3 Refined Tower #2 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011NE552_RF | DI | TRUE
TM140011NE552 | M | MCC | TM140011NE552_RY | Cons.Trans 2. After NBKP #3 Refined Tower #2 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011NE552_RY | DI | TRUE
TM140011NE552 | M | MCC | TM140011NE552_STR | Cons.Trans 2. After NBKP #3 Refined Tower #2 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011NE552_STR | #N/A | #N/A
TM140011NE562 | M | MCC | TM140011NE562_RF | Cons.Trans 3. After NBKP #3 Refined Tower #2 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011NE562_RF | DI | TRUE
TM140011NE562 | M | MCC | TM140011NE562_RY | Cons.Trans 3. After NBKP #3 Refined Tower #2 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011NE562_RY | DI | TRUE
TM140011NE562 | M | MCC | TM140011NE562_STR | Cons.Trans 3. After NBKP #3 Refined Tower #2 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011NE562_STR | #N/A | #N/A
TM140011NE572 | M | MCC | TM140011NE572_RF | Cons.Trans 4. After NBKP #3 Refined Tower #2 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011NE572_RF | DI | TRUE
TM140011NE572 | M | MCC | TM140011NE572_RY | Cons.Trans 4. After NBKP #3 Refined Tower #2 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011NE572_RY | DI | TRUE
TM140011NE572 | M | MCC | TM140011NE572_STR | Cons.Trans 4. After NBKP #3 Refined Tower #2 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011NE572_STR | #N/A | #N/A
TM140011U001M1 | M | MCC | TM140011U001M1_CURR | Pump NBKP#3 Pulper Discharge | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011U001M1_CURR | AI | TRUE
TM140011U001M1 | M | MCC | TM140011U001M1_RF | Pump NBKP#3 Pulper Discharge | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011U001M1_RF | DI | TRUE
TM140011U001M1 | M | MCC | TM140011U001M1_RY | Pump NBKP#3 Pulper Discharge | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011U001M1_RY | DI | TRUE
TM140011U001M1 | M | MCC | TM140011U001M1_STR | Pump NBKP#3 Pulper Discharge | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011U001M1_STR | #N/A | #N/A
TM140011U002M1 | M | MCC | TM140011U002M1_CURR | Pump Feed HD Cleaner | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011U002M1_CURR | AI | TRUE
TM140011U002M1 | M | MCC | TM140011U002M1_RF | Pump Feed HD Cleaner | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011U002M1_RF | DI | TRUE
TM140011U002M1 | M | MCC | TM140011U002M1_RY | Pump Feed HD Cleaner | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011U002M1_RY | DI | TRUE
TM140011U002M1 | M | MCC | TM140011U002M1_STR | Pump Feed HD Cleaner | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011U002M1_STR | #N/A | #N/A
TM140011U003M1 | M | MCC | TM140011U003M1_CURR | Pump #1 NBKP #3 Refined Tower #1 | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011U003M1_CURR | AI | TRUE
TM140011U003M1 | M | MCC | TM140011U003M1_RF | Pump #1 NBKP #3 Refined Tower #1 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011U003M1_RF | DI | TRUE
TM140011U003M1 | M | MCC | TM140011U003M1_RY | Pump #1 NBKP #3 Refined Tower #1 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011U003M1_RY | DI | TRUE
TM140011U003M1 | M | MCC | TM140011U003M1_STR | Pump #1 NBKP #3 Refined Tower #1 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011U003M1_STR | #N/A | #N/A
TM140011U004M1 | M | MCC | TM140011U004M1_CURR | Pump #2 NBKP #3 Refined Tower #1 | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011U004M1_CURR | AI | TRUE
TM140011U004M1 | M | MCC | TM140011U004M1_RF | Pump #2 NBKP #3 Refined Tower #1 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011U004M1_RF | DI | TRUE
TM140011U004M1 | M | MCC | TM140011U004M1_RY | Pump #2 NBKP #3 Refined Tower #1 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011U004M1_RY | DI | TRUE
TM140011U004M1 | M | MCC | TM140011U004M1_STR | Pump #2 NBKP #3 Refined Tower #1 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011U004M1_STR | #N/A | #N/A
TM140011U005M1 | M | MCC | TM140011U005M1_CURR | Pump #3 NBKP #3 Refined Tower #1 | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011U005M1_CURR | AI | TRUE
TM140011U005M1 | M | MCC | TM140011U005M1_RF | Pump #3 NBKP #3 Refined Tower #1 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011U005M1_RF | DI | TRUE
TM140011U005M1 | M | MCC | TM140011U005M1_RY | Pump #3 NBKP #3 Refined Tower #1 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011U005M1_RY | DI | TRUE
TM140011U005M1 | M | MCC | TM140011U005M1_STR | Pump #3 NBKP #3 Refined Tower #1 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011U005M1_STR | #N/A | #N/A
TM140011U006M1 | M | MCC | TM140011U006M1_CURR | Pump #4 NBKP #3 Refined Tower #1 | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011U006M1_CURR | AI | TRUE
TM140011U006M1 | M | MCC | TM140011U006M1_RF | Pump #4 NBKP #3 Refined Tower #1 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011U006M1_RF | DI | TRUE
TM140011U006M1 | M | MCC | TM140011U006M1_RY | Pump #4 NBKP #3 Refined Tower #1 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011U006M1_RY | DI | TRUE
TM140011U006M1 | M | MCC | TM140011U006M1_STR | Pump #4 NBKP #3 Refined Tower #1 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011U006M1_STR | #N/A | #N/A
TM140011U007M1 | M | MCC | TM140011U007M1_CURR | Pump #1 NBKP #3 Refined Tower #2 | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011U007M1_CURR | AI | TRUE
TM140011U007M1 | M | MCC | TM140011U007M1_RF | Pump #1 NBKP #3 Refined Tower #2 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011U007M1_RF | DI | TRUE
TM140011U007M1 | M | MCC | TM140011U007M1_RY | Pump #1 NBKP #3 Refined Tower #2 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011U007M1_RY | DI | TRUE
TM140011U007M1 | M | MCC | TM140011U007M1_STR | Pump #1 NBKP #3 Refined Tower #2 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011U007M1_STR | #N/A | #N/A
TM140011U008M1 | M | MCC | TM140011U008M1_CURR | Pump #2 NBKP #3 Refined Tower #2 | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011U008M1_CURR | AI | TRUE
TM140011U008M1 | M | MCC | TM140011U008M1_RF | Pump #2 NBKP #3 Refined Tower #2 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011U008M1_RF | DI | TRUE
TM140011U008M1 | M | MCC | TM140011U008M1_RY | Pump #2 NBKP #3 Refined Tower #2 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011U008M1_RY | DI | TRUE
TM140011U008M1 | M | MCC | TM140011U008M1_STR | Pump #2 NBKP #3 Refined Tower #2 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011U008M1_STR | #N/A | #N/A
TM140011U009M1 | M | MCC | TM140011U009M1_CURR | Pump #3 NBKP #3 Refined Tower #2 | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011U009M1_CURR | AI | TRUE
TM140011U009M1 | M | MCC | TM140011U009M1_RF | Pump #3 NBKP #3 Refined Tower #2 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011U009M1_RF | DI | TRUE
TM140011U009M1 | M | MCC | TM140011U009M1_RY | Pump #3 NBKP #3 Refined Tower #2 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011U009M1_RY | DI | TRUE
TM140011U009M1 | M | MCC | TM140011U009M1_STR | Pump #3 NBKP #3 Refined Tower #2 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011U009M1_STR | #N/A | #N/A
TM140011U010M1 | M | MCC | TM140011U010M1_CURR | Pump #4 NBKP #3 Refined Tower #2 | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140011U010M1_CURR | AI | TRUE
TM140011U010M1 | M | MCC | TM140011U010M1_RF | Pump #4 NBKP #3 Refined Tower #2 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140011U010M1_RF | DI | TRUE
TM140011U010M1 | M | MCC | TM140011U010M1_RY | Pump #4 NBKP #3 Refined Tower #2 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140011U010M1_RY | DI | TRUE
TM140011U010M1 | M | MCC | TM140011U010M1_STR | Pump #4 NBKP #3 Refined Tower #2 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140011U010M1_STR | #N/A | #N/A
TM140021U002M1 | M | MCC | TM140021U002M1_CURR | Pump Pulping Filling Water | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140021U002M1_CURR | AI | TRUE
TM140021U002M1 | M | MCC | TM140021U002M1_RF | Pump Pulping Filling Water | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140021U002M1_RF | DI | TRUE
TM140021U002M1 | M | MCC | TM140021U002M1_RY | Pump Pulping Filling Water | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140021U002M1_RY | DI | TRUE
TM140021U002M1 | M | MCC | TM140021U002M1_STR | Pump Pulping Filling Water | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140021U002M1_STR | #N/A | #N/A
TM140117A001M1 | M | MCC | TM140117A001M1_CURR | Agitator Broke Deflaker Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140117A001M1_CURR | AI | TRUE
TM140117A001M1 | M | MCC | TM140117A001M1_RF | Agitator Broke Deflaker Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140117A001M1_RF | DI | TRUE
TM140117A001M1 | M | MCC | TM140117A001M1_RY | Agitator Broke Deflaker Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140117A001M1_RY | DI | TRUE
TM140117A001M1 | M | MCC | TM140117A001M1_STR | Agitator Broke Deflaker Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140117A001M1_STR | #N/A | #N/A
TM140117A002M1 | M | MCC | TM140117A002M1_CURR | Agitator Broke Thickened Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140117A002M1_CURR | AI | TRUE
TM140117A002M1 | M | MCC | TM140117A002M1_RF | Agitator Broke Thickened Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140117A002M1_RF | DI | TRUE
TM140117A002M1 | M | MCC | TM140117A002M1_RY | Agitator Broke Thickened Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140117A002M1_RY | DI | TRUE
TM140117A002M1 | M | MCC | TM140117A002M1_STR | Agitator Broke Thickened Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140117A002M1_STR | #N/A | #N/A
TM140117A003M1 | M | MCC | TM140117A003M1_CURR | Agitator Broke Interim Tower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140117A003M1_CURR | AI | TRUE
TM140117A003M1 | M | MCC | TM140117A003M1_RF | Agitator Broke Interim Tower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140117A003M1_RF | DI | TRUE
TM140117A003M1 | M | MCC | TM140117A003M1_RY | Agitator Broke Interim Tower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DO | Ready signal should be DI | _RY | TM140117A003M1_RY | DI | FALSE
TM140117A003M1 | M | MCC | TM140117A003M1_STR | Agitator Broke Interim Tower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140117A003M1_STR | #N/A | #N/A
TM140117M001M1 | M | MCC | TM140117M001M1_CURR | Deflaker | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140117M001M1_CURR | AI | TRUE
TM140117M001M1 | M | MCC | TM140117M001M1_RF | Deflaker | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140117M001M1_RF | DI | TRUE
TM140117M001M1 | M | MCC | TM140117M001M1_RY | Deflaker | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140117M001M1_RY | DI | TRUE
TM140117M001M1 | M | MCC | TM140117M001M1_STR | Deflaker | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140117M001M1_STR | #N/A | #N/A
TM140117M004M1 | M | MCC | TM140117M004M1_CURR | Agitator Yankee Pulper | ET | DCS | Actual Current | 0 | 130 | % | Profibus |  |  | BUS | AI |  | _CURR | TM140117M004M1_CURR | AI | TRUE
TM140117M004M1 | M | MCC | TM140117M004M1_RF | Agitator Yankee Pulper | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140117M004M1_RF | DI | TRUE
TM140117M004M1 | M | MCC | TM140117M004M1_RY | Agitator Yankee Pulper | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140117M004M1_RY | DI | TRUE
TM140117M004M1 | M | MCC | TM140117M004M1_STR | Agitator Yankee Pulper | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140117M004M1_STR | #N/A | #N/A
TM140117NE044 | M | MCC | TM140117NE044_RF | Cons.Trans. After Broke Deflaker Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140117NE044_RF | DI | TRUE
TM140117NE044 | M | MCC | TM140117NE044_RY | Cons.Trans. After Broke Deflaker Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140117NE044_RY | DI | TRUE
TM140117NE044 | M | MCC | TM140117NE044_STR | Cons.Trans. After Broke Deflaker Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140117NE044_STR | #N/A | #N/A
TM140117NE091 | M | MCC | TM140117NE091_RF | Cons.Trans. After Thickened Broke Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140117NE091_RF | DI | TRUE
TM140117NE091 | M | MCC | TM140117NE091_RY | Cons.Trans. After Thickened Broke Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140117NE091_RY | DI | TRUE
TM140117NE091 | M | MCC | TM140117NE091_STR | Cons.Trans. After Thickened Broke Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140117NE091_STR | #N/A | #N/A
TM140117U001M1 | M | MCC | TM140117U001M1_CURR | Pump Broke Deflaker Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140117U001M1_CURR | AI | TRUE
TM140117U001M1 | M | MCC | TM140117U001M1_RF | Pump Broke Deflaker Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140117U001M1_RF | DI | TRUE
TM140117U001M1 | M | MCC | TM140117U001M1_RY | Pump Broke Deflaker Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140117U001M1_RY | DI | TRUE
TM140117U001M1 | M | MCC | TM140117U001M1_STR | Pump Broke Deflaker Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140117U001M1_STR | #N/A | #N/A
TM140117U002M1 | M | MCC | TM140117U002M1_CURR | Pump Broke Thickened Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140117U002M1_CURR | AI | TRUE
TM140117U002M1 | M | MCC | TM140117U002M1_RF | Pump Broke Thickened Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140117U002M1_RF | DI | TRUE
TM140117U002M1 | M | MCC | TM140117U002M1_RY | Pump Broke Thickened Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140117U002M1_RY | DI | TRUE
TM140117U002M1 | M | MCC | TM140117U002M1_STR | Pump Broke Thickened Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140117U002M1_STR | #N/A | #N/A
TM140117U003M1 | M | MCC | TM140117U003M1_CURR | Pump 1 Broke Interim Tower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140117U003M1_CURR | AI | TRUE
TM140117U003M1 | M | MCC | TM140117U003M1_RF | Pump 1 Broke Interim Tower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140117U003M1_RF | DI | TRUE
TM140117U003M1 | M | MCC | TM140117U003M1_RY | Pump 1 Broke Interim Tower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140117U003M1_RY | DI | TRUE
TM140117U003M1 | M | MCC | TM140117U003M1_STR | Pump 1 Broke Interim Tower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140117U003M1_STR | #N/A | #N/A
TM140117U004M1 | M | MCC | TM140117U004M1_CURR | Pump 2 Broke Interim Tower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140117U004M1_CURR | AI | TRUE
TM140117U004M1 | M | MCC | TM140117U004M1_RF | Pump 2 Broke Interim Tower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140117U004M1_RF | DI | TRUE
TM140117U004M1 | M | MCC | TM140117U004M1_RY | Pump 2 Broke Interim Tower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140117U004M1_RY | DI | TRUE
TM140117U004M1 | M | MCC | TM140117U004M1_STR | Pump 2 Broke Interim Tower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140117U004M1_STR | #N/A | #N/A
TM140117U005M1 | M | MCC | TM140117U005M1_CURR | Pump Yankee Pulper | ET | DCS | Actual Current | 0 | 130 | % | Profibus |  |  | BUS | AI |  | _CURR | TM140117U005M1_CURR | AI | TRUE
TM140117U005M1 | M | MCC | TM140117U005M1_RF | Pump Yankee Pulper | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140117U005M1_RF | DI | TRUE
TM140117U005M1 | M | MCC | TM140117U005M1_RY | Pump Yankee Pulper | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140117U005M1_RY | DI | TRUE
TM140117U005M1 | M | MCC | TM140117U005M1_STR | Pump Yankee Pulper | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140117U005M1_STR | #N/A | #N/A
TM140117U006M1 | M | MCC | TM140117U006M1_CURR | Pump Yankee Pulper Recirculation | ET | DCS | Actual Current | 0 | 130 | % | Profibus |  |  | BUS | AI |  | _CURR | TM140117U006M1_CURR | AI | TRUE
TM140117U006M1 | M | MCC | TM140117U006M1_RF | Pump Yankee Pulper Recirculation | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140117U006M1_RF | DI | TRUE
TM140117U006M1 | M | MCC | TM140117U006M1_RY | Pump Yankee Pulper Recirculation | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140117U006M1_RY | DI | TRUE
TM140117U006M1 | M | MCC | TM140117U006M1_STR | Pump Yankee Pulper Recirculation | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140117U006M1_STR | #N/A | #N/A
TM140133F002M1 | M | MCC | TM140133F002M1_RF | Exhaust Fan Yankee Pulper | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140133F002M1_RF | DI | TRUE
TM140133F002M1 | M | MCC | TM140133F002M1_RY | Exhaust Fan Yankee Pulper | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DO | Ready signal should be DI | _RY | TM140133F002M1_RY | DI | FALSE
TM140133F002M1 | M | MCC | TM140133F002M1_STR | Exhaust Fan Yankee Pulper | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140133F002M1_STR | #N/A | #N/A
TM140120A001M1 | M | MCC | TM140120A001M1_CURR | Agitator Mixing Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140120A001M1_CURR | AI | TRUE
TM140120A001M1 | M | MCC | TM140120A001M1_RF | Agitator Mixing Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140120A001M1_RF | DI | TRUE
TM140120A001M1 | M | MCC | TM140120A001M1_RY | Agitator Mixing Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140120A001M1_RY | DI | TRUE
TM140120A001M1 | M | MCC | TM140120A001M1_STR | Agitator Mixing Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140120A001M1_STR | #N/A | #N/A
TM140120A002M1 | M | MCC | TM140120A002M1_CURR | Agitator Machine Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140120A002M1_CURR | AI | TRUE
TM140120A002M1 | M | MCC | TM140120A002M1_RF | Agitator Machine Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140120A002M1_RF | DI | TRUE
TM140120A002M1 | M | MCC | TM140120A002M1_RY | Agitator Machine Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140120A002M1_RY | DI | TRUE
TM140120A002M1 | M | MCC | TM140120A002M1_STR | Agitator Machine Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140120A002M1_STR | #N/A | #N/A
TM140120M001M1 | M | MCC | TM140120M001M1_CURR | Tickler Refiner TF-26 | ET | DCS | Actual Current | 0 | 120 | % | Profibus |  |  | BUS | AI |  | _CURR | TM140120M001M1_CURR | AI | TRUE
TM140120M001M1 | M | MCC | TM140120M001M1_FLT | Tickler Refiner TF-26 | K4 | DCS | Fault |  |  |  | Profibus |  |  | BUS | DI |  | _FLT | TM140120M001M1_FLT | DI | TRUE
TM140120M001M1 | M | MCC | TM140120M001M1_RY | Tickler Refiner TF-26 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140120M001M1_RY | DI | TRUE
TM140120M001M1 | M | MCC | TM140120M001M1_STR | Tickler Refiner TF-26 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140120M001M1_STR | #N/A | #N/A
TM140120M001M2 | M | MCC | TM140120M001M2_RF | Plate Adjustment Refiner | K1 | DCS | Run = 1 |  |  |  | Dry Contact | NO | 24 VDC | HW | DI |  | _RF | TM140120M001M2_RF | DI | TRUE
TM140120M001M2 | M | MCC | TM140120M001M2_RY | Plate Adjustment Refiner | K5 | DCS | Ready = 1 |  |  |  | Dry Contact | NO | 24 VDC | HW | DI |  | _RY | TM140120M001M2_RY | DI | TRUE
TM140120M001M2 | M | MCC | TM140120M001M2_STR | Plate Adjustment Refiner | K11 | DCS | Load Start |  |  |  | Dry Contact | NO | 24 VDC | HW | DO |  | _STR | TM140120M001M2_STR | #N/A | #N/A
TM140120M001M2 | M | MCC | TM140120M001M2_STR | Plate Adjustment Refiner | K12 | DCS | Release Start |  |  |  | Dry Contact | NO | 24 VDC | HW | DO |  | _STR | TM140120M001M2_STR | DO | TRUE
TM140120NE012 | M | MCC | TM140120NE012_RF | Cons.Trans. After P. Mixing Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140120NE012_RF | DI | TRUE
TM140120NE012 | M | MCC | TM140120NE012_RY | Cons.Trans. After P. Mixing Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140120NE012_RY | DI | TRUE
TM140120NE012 | M | MCC | TM140120NE012_STR | Cons.Trans. After P. Mixing Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140120NE012_STR | #N/A | #N/A
TM140120NE053 | M | MCC | TM140120NE053_RF | Cons.Trans. After P. Machine Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140120NE053_RF | DI | TRUE
TM140120NE053 | M | MCC | TM140120NE053_RY | Cons.Trans. After P. Machine Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140120NE053_RY | DI | TRUE
TM140120NE053 | M | MCC | TM140120NE053_STR | Cons.Trans. After P. Machine Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140120NE053_STR | #N/A | #N/A
TM140120U001M1 | M | MCC | TM140120U001M1_CURR | Pump#1 Mixing Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140120U001M1_CURR | AI | TRUE
TM140120U001M1 | M | MCC | TM140120U001M1_RF | Pump#1 Mixing Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140120U001M1_RF | DI | TRUE
TM140120U001M1 | M | MCC | TM140120U001M1_RY | Pump#1 Mixing Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140120U001M1_RY | DI | TRUE
TM140120U001M1 | M | MCC | TM140120U001M1_STR | Pump#1 Mixing Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140120U001M1_STR | #N/A | #N/A
TM140120U002M1 | M | MCC | TM140120U002M1_CURR | Pump#2 Mixing Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140120U002M1_CURR | AI | TRUE
TM140120U002M1 | M | MCC | TM140120U002M1_RF | Pump#2 Mixing Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140120U002M1_RF | DI | TRUE
TM140120U002M1 | M | MCC | TM140120U002M1_RY | Pump#2 Mixing Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140120U002M1_RY | DI | TRUE
TM140120U002M1 | M | MCC | TM140120U002M1_STR | Pump#2 Mixing Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140120U002M1_STR | #N/A | #N/A
TM140120U003M1 | M | MCC | TM140120U003M1_CURR | Pump Sweetener | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140120U003M1_CURR | AI | TRUE
TM140120U003M1 | M | MCC | TM140120U003M1_RF | Pump Sweetener | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140120U003M1_RF | DI | TRUE
TM140120U003M1 | M | MCC | TM140120U003M1_RY | Pump Sweetener | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140120U003M1_RY | DI | TRUE
TM140120U003M1 | M | MCC | TM140120U003M1_STR | Pump Sweetener | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140120U003M1_STR | #N/A | #N/A
TM140120U004M1 | M | MCC | TM140120U004M1_CURR | Pump#1 Machine Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140120U004M1_CURR | AI | TRUE
TM140120U004M1 | M | MCC | TM140120U004M1_RF | Pump#1 Machine Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140120U004M1_RF | DI | TRUE
TM140120U004M1 | M | MCC | TM140120U004M1_RY | Pump#1 Machine Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140120U004M1_RY | DI | TRUE
TM140120U004M1 | M | MCC | TM140120U004M1_STR | Pump#1 Machine Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140120U004M1_STR | #N/A | #N/A
TM140120U005M1 | M | MCC | TM140120U005M1_CURR | Pump#2 Machine Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140120U005M1_CURR | AI | TRUE
TM140120U005M1 | M | MCC | TM140120U005M1_RF | Pump#2 Machine Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140120U005M1_RF | DI | TRUE
TM140120U005M1 | M | MCC | TM140120U005M1_RY | Pump#2 Machine Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140120U005M1_RY | DI | TRUE
TM140120U005M1 | M | MCC | TM140120U005M1_STR | Pump#2 Machine Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140120U005M1_STR | #N/A | #N/A
TM140120S001M1 | M | MCC | TM140120S001M1_CURR | 1.Stage Headbox Screen | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140120S001M1_CURR | AI | TRUE
TM140120S001M1 | M | MCC | TM140120S001M1_RF | 1.Stage Headbox Screen | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140120S001M1_RF | DI | TRUE
TM140120S001M1 | M | MCC | TM140120S001M1_RY | 1.Stage Headbox Screen | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140120S001M1_RY | DI | TRUE
TM140120S001M1 | M | MCC | TM140120S001M1_STR | 1.Stage Headbox Screen | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140120S001M1_STR | #N/A | #N/A
TM140120S002M1 | M | MCC | TM140120S002M1_CURR | 2.Stage Headbox Screen | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140120S002M1_CURR | AI | TRUE
TM140120S002M1 | M | MCC | TM140120S002M1_RF | 2.Stage Headbox Screen | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140120S002M1_RF | DI | TRUE
TM140120S002M1 | M | MCC | TM140120S002M1_RY | 2.Stage Headbox Screen | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140120S002M1_RY | DI | TRUE
TM140120S002M1 | M | MCC | TM140120S002M1_STR | 2.Stage Headbox Screen | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140120S002M1_STR | #N/A | #N/A
TM140120U006M1 | M | MCC | TM140120U006M1_CURR | Fan Pump | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140120U006M1_CURR | AI | TRUE
TM140120U006M1 | M | MCC | TM140120U006M1_RF | Fan Pump | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140120U006M1_RF | DI | TRUE
TM140120U006M1 | M | MCC | TM140120U006M1_RY | Fan Pump | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140120U006M1_RY | DI | TRUE
TM140120U006M1 | M | MCC | TM140120U006M1_STR | Fan Pump | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140120U006M1_STR | #N/A | #N/A
TM140120U007M1 | M | MCC | TM140120U007M1_CURR | Pump Wire Water Water Tank | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140120U007M1_CURR | AI | TRUE
TM140120U007M1 | M | MCC | TM140120U007M1_RF | Pump Wire Water Water Tank | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140120U007M1_RF | DI | TRUE
TM140120U007M1 | M | MCC | TM140120U007M1_RY | Pump Wire Water Water Tank | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140120U007M1_RY | DI | TRUE
TM140120U007M1 | M | MCC | TM140120U007M1_STR | Pump Wire Water Water Tank | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140120U007M1_STR | #N/A | #N/A
TM140121A005M1 | M | MCC | TM140121A005M1_CURR | Agitator Recovered Fiber Tank | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140121A005M1_CURR | AI | TRUE
TM140121A005M1 | M | MCC | TM140121A005M1_RF | Agitator Recovered Fiber Tank | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140121A005M1_RF | DI | TRUE
TM140121A005M1 | M | MCC | TM140121A005M1_RY | Agitator Recovered Fiber Tank | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140121A005M1_RY | DI | TRUE
TM140121A005M1 | M | MCC | TM140121A005M1_STR | Agitator Recovered Fiber Tank | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140121A005M1_STR | #N/A | #N/A
TM140121M001M1 | M | MCC | TM140121M001M1_CURR | Disc Filter | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140121M001M1_CURR | AI | TRUE
TM140121M001M1 | M | MCC | TM140121M001M1_RF | Disc Filter | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140121M001M1_RF | DI | TRUE
TM140121M001M1 | M | MCC | TM140121M001M1_RY | Disc Filter | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140121M001M1_RY | DI | TRUE
TM140121M001M1 | M | MCC | TM140121M001M1_STR | Disc Filter | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140121M001M1_STR | #N/A | #N/A
TM140121M001M2 | M | MCC | TM140121M001M2_CURR | Shower Oscillation Disc Filter | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140121M001M2_CURR | AI | TRUE
TM140121M001M2 | M | MCC | TM140121M001M2_RF | Shower Oscillation Disc Filter | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140121M001M2_RF | DI | TRUE
TM140121M001M2 | M | MCC | TM140121M001M2_RY | Shower Oscillation Disc Filter | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140121M001M2_RY | DI | TRUE
TM140121M001M2 | M | MCC | TM140121M001M2_STR | Shower Oscillation Disc Filter | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140121M001M2_STR | #N/A | #N/A
TM140121M001M3 | M | MCC | TM140121M001M3_CURR | Repulper Disc Filter | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140121M001M3_CURR | AI | TRUE
TM140121M001M3 | M | MCC | TM140121M001M3_RF | Repulper Disc Filter | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140121M001M3_RF | DI | TRUE
TM140121M001M3 | M | MCC | TM140121M001M3_RY | Repulper Disc Filter | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140121M001M3_RY | DI | TRUE
TM140121M001M3 | M | MCC | TM140121M001M3_STR | Repulper Disc Filter | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140121M001M3_STR | #N/A | #N/A
TM140121NE138 | M | MCC | TM140121NE138_RF | Cons.Trans. After Recovery Fibre Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140121NE138_RF | DI | TRUE
TM140121NE138 | M | MCC | TM140121NE138_RY | Cons.Trans. After Recovery Fibre Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140121NE138_RY | DI | TRUE
TM140121NE138 | M | MCC | TM140121NE138_STR | Cons.Trans. After Recovery Fibre Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140121NE138_STR | #N/A | #N/A
TM140121U001M1 | M | MCC | TM140121U001M1_CURR | Pump White Water | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140121U001M1_CURR | AI | TRUE
TM140121U001M1 | M | MCC | TM140121U001M1_RF | Pump White Water | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140121U001M1_RF | DI | TRUE
TM140121U001M1 | M | MCC | TM140121U001M1_RY | Pump White Water | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140121U001M1_RY | DI | TRUE
TM140121U001M1 | M | MCC | TM140121U001M1_STR | Pump White Water | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140121U001M1_STR | #N/A | #N/A
TM140121U002M1 | M | MCC | TM140121U002M1_CURR | Pump TM Area CRC | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140121U002M1_CURR | AI | TRUE
TM140121U002M1 | M | MCC | TM140121U002M1_RF | Pump TM Area CRC | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140121U002M1_RF | DI | TRUE
TM140121U002M1 | M | MCC | TM140121U002M1_RY | Pump TM Area CRC | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140121U002M1_RY | DI | TRUE
TM140121U002M1 | M | MCC | TM140121U002M1_STR | Pump TM Area CRC | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140121U002M1_STR | #N/A | #N/A
TM140121U003M1 | M | MCC | TM140121U003M1_CURR | Pump Yankee Pulping /Over flow | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140121U003M1_CURR | AI | TRUE
TM140121U003M1 | M | MCC | TM140121U003M1_RF | Pump Yankee Pulping /Over flow | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140121U003M1_RF | DI | TRUE
TM140121U003M1 | M | MCC | TM140121U003M1_RY | Pump Yankee Pulping /Over flow | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140121U003M1_RY | DI | TRUE
TM140121U003M1 | M | MCC | TM140121U003M1_STR | Pump Yankee Pulping /Over flow | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140121U003M1_STR | #N/A | #N/A
TM140121U004M1 | M | MCC | TM140121U004M1_CURR | Pump Recovered Fiber | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140121U004M1_CURR | AI | TRUE
TM140121U004M1 | M | MCC | TM140121U004M1_RF | Pump Recovered Fiber | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140121U004M1_RF | DI | TRUE
TM140121U004M1 | M | MCC | TM140121U004M1_RY | Pump Recovered Fiber | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140121U004M1_RY | DI | TRUE
TM140121U004M1 | M | MCC | TM140121U004M1_STR | Pump Recovered Fiber | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140121U004M1_STR | #N/A | #N/A
TM140121U005M1 | M | MCC | TM140121U005M1_CURR | Pump Cloudy Filtrate | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140121U005M1_CURR | AI | TRUE
TM140121U005M1 | M | MCC | TM140121U005M1_RF | Pump Cloudy Filtrate | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140121U005M1_RF | DI | TRUE
TM140121U005M1 | M | MCC | TM140121U005M1_RY | Pump Cloudy Filtrate | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140121U005M1_RY | DI | TRUE
TM140121U005M1 | M | MCC | TM140121U005M1_STR | Pump Cloudy Filtrate | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140121U005M1_STR | #N/A | #N/A
TM140121U006M1 | M | MCC | TM140121U006M1_CURR | Pump CWW HP Shower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140121U006M1_CURR | AI | TRUE
TM140121U006M1 | M | MCC | TM140121U006M1_RF | Pump CWW HP Shower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140121U006M1_RF | DI | TRUE
TM140121U006M1 | M | MCC | TM140121U006M1_RY | Pump CWW HP Shower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140121U006M1_RY | DI | TRUE
TM140121U006M1 | M | MCC | TM140121U006M1_STR | Pump CWW HP Shower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140121U006M1_STR | #N/A | #N/A
TM140121U007M1 | M | MCC | TM140121U007M1_CURR | Pump Clear Filtrate | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140121U007M1_CURR | AI | TRUE
TM140121U007M1 | M | MCC | TM140121U007M1_RF | Pump Clear Filtrate | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140121U007M1_RF | DI | TRUE
TM140121U007M1 | M | MCC | TM140121U007M1_RY | Pump Clear Filtrate | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140121U007M1_RY | DI | TRUE
TM140121U007M1 | M | MCC | TM140121U007M1_STR | Pump Clear Filtrate | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140121U007M1_STR | #N/A | #N/A
TM140121U008M1 | M | MCC | TM140121U008M1_CURR | Pump Disc Filter Shower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140121U008M1_CURR | AI | TRUE
TM140121U008M1 | M | MCC | TM140121U008M1_RF | Pump Disc Filter Shower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140121U008M1_RF | DI | TRUE
TM140121U008M1 | M | MCC | TM140121U008M1_RY | Pump Disc Filter Shower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140121U008M1_RY | DI | TRUE
TM140121U008M1 | M | MCC | TM140121U008M1_STR | Pump Disc Filter Shower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140121U008M1_STR | #N/A | #N/A
TM140121U009M1 | M | MCC | TM140121U009M1_CURR | Pump CWW LP Shower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140121U009M1_CURR | AI | TRUE
TM140121U009M1 | M | MCC | TM140121U009M1_RF | Pump CWW LP Shower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140121U009M1_RF | DI | TRUE
TM140121U009M1 | M | MCC | TM140121U009M1_RY | Pump CWW LP Shower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140121U009M1_RY | DI | TRUE
TM140121U009M1 | M | MCC | TM140121U009M1_STR | Pump CWW LP Shower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140121U009M1_STR | #N/A | #N/A
TM140121U011M1 | M | MCC | TM140121U011M1_CURR | Pump SCWW LP Shower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140121U011M1_CURR | AI | TRUE
TM140121U011M1 | M | MCC | TM140121U011M1_RF | Pump SCWW LP Shower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140121U011M1_RF | DI | TRUE
TM140121U011M1 | M | MCC | TM140121U011M1_RY | Pump SCWW LP Shower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140121U011M1_RY | DI | TRUE
TM140121U011M1 | M | MCC | TM140121U011M1_STR | Pump SCWW LP Shower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140121U011M1_STR | #N/A | #N/A
TM140121U012M1 | M | MCC | TM140121U012M1_CURR | Pump CWW Cleaning | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140121U012M1_CURR | AI | TRUE
TM140121U012M1 | M | MCC | TM140121U012M1_RF | Pump CWW Cleaning | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140121U012M1_RF | DI | TRUE
TM140121U012M1 | M | MCC | TM140121U012M1_RY | Pump CWW Cleaning | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140121U012M1_RY | DI | TRUE
TM140121U012M1 | M | MCC | TM140121U012M1_STR | Pump CWW Cleaning | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140121U012M1_STR | #N/A | #N/A
TM140121U013M1 | M | MCC | TM140121U013M1_CURR | Pump SCWW HP Shower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140121U013M1_CURR | AI | TRUE
TM140121U013M1 | M | MCC | TM140121U013M1_RF | Pump SCWW HP Shower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140121U013M1_RF | DI | TRUE
TM140121U013M1 | M | MCC | TM140121U013M1_RY | Pump SCWW HP Shower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140121U013M1_RY | DI | TRUE
TM140121U013M1 | M | MCC | TM140121U013M1_STR | Pump SCWW HP Shower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140121U013M1_STR | #N/A | #N/A
TM140217A001M1 | M | MCC | TM140217A001M1_CURR | Agitator Broke Deflaker Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140217A001M1_CURR | AI | TRUE
TM140217A001M1 | M | MCC | TM140217A001M1_RF | Agitator Broke Deflaker Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140217A001M1_RF | DI | TRUE
TM140217A001M1 | M | MCC | TM140217A001M1_RY | Agitator Broke Deflaker Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140217A001M1_RY | DI | TRUE
TM140217A001M1 | M | MCC | TM140217A001M1_STR | Agitator Broke Deflaker Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140217A001M1_STR | #N/A | #N/A
TM140217A002M1 | M | MCC | TM140217A002M1_CURR | Agitator Broke Thickened Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140217A002M1_CURR | AI | TRUE
TM140217A002M1 | M | MCC | TM140217A002M1_RF | Agitator Broke Thickened Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140217A002M1_RF | DI | TRUE
TM140217A002M1 | M | MCC | TM140217A002M1_RY | Agitator Broke Thickened Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140217A002M1_RY | DI | TRUE
TM140217A002M1 | M | MCC | TM140217A002M1_STR | Agitator Broke Thickened Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140217A002M1_STR | #N/A | #N/A
TM140217A003M1 | M | MCC | TM140217A003M1_CURR | Agitator Broke Interim Tower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140217A003M1_CURR | AI | TRUE
TM140217A003M1 | M | MCC | TM140217A003M1_RF | Agitator Broke Interim Tower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140217A003M1_RF | DI | TRUE
TM140217A003M1 | M | MCC | TM140217A003M1_RY | Agitator Broke Interim Tower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DO | Ready signal should be DI | _RY | TM140217A003M1_RY | DI | FALSE
TM140217A003M1 | M | MCC | TM140217A003M1_STR | Agitator Broke Interim Tower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140217A003M1_STR | #N/A | #N/A
TM140217M001M1 | M | MCC | TM140217M001M1_CURR | Deflaker | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140217M001M1_CURR | AI | TRUE
TM140217M001M1 | M | MCC | TM140217M001M1_RF | Deflaker | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140217M001M1_RF | DI | TRUE
TM140217M001M1 | M | MCC | TM140217M001M1_RY | Deflaker | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140217M001M1_RY | DI | TRUE
TM140217M001M1 | M | MCC | TM140217M001M1_STR | Deflaker | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140217M001M1_STR | #N/A | #N/A
TM140217M004M1 | M | MCC | TM140217M004M1_CURR | Agitator Yankee Pulper | ET | DCS | Actual Current | 0 | 130 | % | Profibus |  |  | BUS | AI |  | _CURR | TM140217M004M1_CURR | AI | TRUE
TM140217M004M1 | M | MCC | TM140217M004M1_RF | Agitator Yankee Pulper | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140217M004M1_RF | DI | TRUE
TM140217M004M1 | M | MCC | TM140217M004M1_RY | Agitator Yankee Pulper | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140217M004M1_RY | DI | TRUE
TM140217M004M1 | M | MCC | TM140217M004M1_STR | Agitator Yankee Pulper | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140217M004M1_STR | #N/A | #N/A
TM140217NE044 | M | MCC | TM140217NE044_RF | Cons.Trans. After Broke Deflaker Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140217NE044_RF | DI | TRUE
TM140217NE044 | M | MCC | TM140217NE044_RY | Cons.Trans. After Broke Deflaker Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140217NE044_RY | DI | TRUE
TM140217NE044 | M | MCC | TM140217NE044_STR | Cons.Trans. After Broke Deflaker Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140217NE044_STR | #N/A | #N/A
TM140217NE091 | M | MCC | TM140217NE091_RF | Cons.Trans. After Thickened Broke Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140217NE091_RF | DI | TRUE
TM140217NE091 | M | MCC | TM140217NE091_RY | Cons.Trans. After Thickened Broke Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140217NE091_RY | DI | TRUE
TM140217NE091 | M | MCC | TM140217NE091_STR | Cons.Trans. After Thickened Broke Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140217NE091_STR | #N/A | #N/A
TM140217U001M1 | M | MCC | TM140217U001M1_CURR | Pump Broke Deflaker Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140217U001M1_CURR | AI | TRUE
TM140217U001M1 | M | MCC | TM140217U001M1_RF | Pump Broke Deflaker Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140217U001M1_RF | DI | TRUE
TM140217U001M1 | M | MCC | TM140217U001M1_RY | Pump Broke Deflaker Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140217U001M1_RY | DI | TRUE
TM140217U001M1 | M | MCC | TM140217U001M1_STR | Pump Broke Deflaker Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140217U001M1_STR | #N/A | #N/A
TM140217U002M1 | M | MCC | TM140217U002M1_CURR | Pump Broke Thickened Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140217U002M1_CURR | AI | TRUE
TM140217U002M1 | M | MCC | TM140217U002M1_RF | Pump Broke Thickened Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140217U002M1_RF | DI | TRUE
TM140217U002M1 | M | MCC | TM140217U002M1_RY | Pump Broke Thickened Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140217U002M1_RY | DI | TRUE
TM140217U002M1 | M | MCC | TM140217U002M1_STR | Pump Broke Thickened Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140217U002M1_STR | #N/A | #N/A
TM140217U003M1 | M | MCC | TM140217U003M1_CURR | Pump 1 Broke Interim Tower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140217U003M1_CURR | AI | TRUE
TM140217U003M1 | M | MCC | TM140217U003M1_RF | Pump 1 Broke Interim Tower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140217U003M1_RF | DI | TRUE
TM140217U003M1 | M | MCC | TM140217U003M1_RY | Pump 1 Broke Interim Tower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140217U003M1_RY | DI | TRUE
TM140217U003M1 | M | MCC | TM140217U003M1_STR | Pump 1 Broke Interim Tower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140217U003M1_STR | #N/A | #N/A
TM140217U005M1 | M | MCC | TM140217U005M1_CURR | Pump Yankee Pulper | ET | DCS | Actual Current | 0 | 130 | % | Profibus |  |  | BUS | AI |  | _CURR | TM140217U005M1_CURR | AI | TRUE
TM140217U005M1 | M | MCC | TM140217U005M1_RF | Pump Yankee Pulper | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140217U005M1_RF | DI | TRUE
TM140217U005M1 | M | MCC | TM140217U005M1_RY | Pump Yankee Pulper | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140217U005M1_RY | DI | TRUE
TM140217U005M1 | M | MCC | TM140217U005M1_STR | Pump Yankee Pulper | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140217U005M1_STR | #N/A | #N/A
TM140217U006M1 | M | MCC | TM140217U006M1_CURR | Pump Yankee Pulper Recirculation | ET | DCS | Actual Current | 0 | 130 | % | Profibus |  |  | BUS | AI |  | _CURR | TM140217U006M1_CURR | AI | TRUE
TM140217U006M1 | M | MCC | TM140217U006M1_RF | Pump Yankee Pulper Recirculation | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140217U006M1_RF | DI | TRUE
TM140217U006M1 | M | MCC | TM140217U006M1_RY | Pump Yankee Pulper Recirculation | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140217U006M1_RY | DI | TRUE
TM140217U006M1 | M | MCC | TM140217U006M1_STR | Pump Yankee Pulper Recirculation | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140217U006M1_STR | #N/A | #N/A
TM140233F002M1 | M | MCC | TM140233F002M1_RF | Exhaust Fan Yankee Pulper | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140233F002M1_RF | DI | TRUE
TM140233F002M1 | M | MCC | TM140233F002M1_RY | Exhaust Fan Yankee Pulper | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DO | Ready signal should be DI | _RY | TM140233F002M1_RY | DI | FALSE
TM140233F002M1 | M | MCC | TM140233F002M1_STR | Exhaust Fan Yankee Pulper | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140233F002M1_STR | #N/A | #N/A
TM140220A001M1 | M | MCC | TM140220A001M1_CURR | Agitator Mixing Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140220A001M1_CURR | AI | TRUE
TM140220A001M1 | M | MCC | TM140220A001M1_RF | Agitator Mixing Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140220A001M1_RF | DI | TRUE
TM140220A001M1 | M | MCC | TM140220A001M1_RY | Agitator Mixing Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140220A001M1_RY | DI | TRUE
TM140220A001M1 | M | MCC | TM140220A001M1_STR | Agitator Mixing Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140220A001M1_STR | #N/A | #N/A
TM140220A002M1 | M | MCC | TM140220A002M1_CURR | Agitator Machine Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140220A002M1_CURR | AI | TRUE
TM140220A002M1 | M | MCC | TM140220A002M1_RF | Agitator Machine Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140220A002M1_RF | DI | TRUE
TM140220A002M1 | M | MCC | TM140220A002M1_RY | Agitator Machine Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140220A002M1_RY | DI | TRUE
TM140220A002M1 | M | MCC | TM140220A002M1_STR | Agitator Machine Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140220A002M1_STR | #N/A | #N/A
TM140220M001M1 | M | MCC | TM140220M001M1_CURR | Tickler Refiner TF-26 | ET | DCS | Actual Current | 0 | 120 | % | Profibus |  |  | BUS | AI |  | _CURR | TM140220M001M1_CURR | AI | TRUE
TM140220M001M1 | M | MCC | TM140220M001M1_FLT | Tickler Refiner TF-26 | K4 | DCS | Fault |  |  |  | Profibus |  |  | BUS | DI |  | _FLT | TM140220M001M1_FLT | DI | TRUE
TM140220M001M1 | M | MCC | TM140220M001M1_RY | Tickler Refiner TF-26 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140220M001M1_RY | DI | TRUE
TM140220M001M1 | M | MCC | TM140220M001M1_STR | Tickler Refiner TF-26 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140220M001M1_STR | #N/A | #N/A
TM140220M001M2 | M | MCC | TM140220M001M2_RF | Plate Adjustment Refiner | K1 | DCS | Run = 1 |  |  |  | Dry Contact | NO | 24 VDC | HW | DI |  | _RF | TM140220M001M2_RF | DI | TRUE
TM140220M001M2 | M | MCC | TM140220M001M2_RY | Plate Adjustment Refiner | K5 | DCS | Ready = 1 |  |  |  | Dry Contact | NO | 24 VDC | HW | DI |  | _RY | TM140220M001M2_RY | DI | TRUE
TM140220M001M2 | M | MCC | TM140220M001M2_STR | Plate Adjustment Refiner | K11 | DCS | Load Start |  |  |  | Dry Contact | NO | 24 VDC | HW | DO |  | _STR | TM140220M001M2_STR | #N/A | #N/A
TM140220M001M2 | M | MCC | TM140220M001M2_STR | Plate Adjustment Refiner | K12 | DCS | Release Start |  |  |  | Dry Contact | NO | 24 VDC | HW | DO |  | _STR | TM140220M001M2_STR | DO | TRUE
TM140220NE012 | M | MCC | TM140220NE012_RF | Cons.Trans. After P. Mixing Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140220NE012_RF | DI | TRUE
TM140220NE012 | M | MCC | TM140220NE012_RY | Cons.Trans. After P. Mixing Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140220NE012_RY | DI | TRUE
TM140220NE012 | M | MCC | TM140220NE012_STR | Cons.Trans. After P. Mixing Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140220NE012_STR | #N/A | #N/A
TM140220NE053 | M | MCC | TM140220NE053_RF | Cons.Trans. After P. Machine Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140220NE053_RF | DI | TRUE
TM140220NE053 | M | MCC | TM140220NE053_RY | Cons.Trans. After P. Machine Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140220NE053_RY | DI | TRUE
TM140220NE053 | M | MCC | TM140220NE053_STR | Cons.Trans. After P. Machine Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140220NE053_STR | #N/A | #N/A
TM140220U001M1 | M | MCC | TM140220U001M1_CURR | Pump#1 Mixing Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140220U001M1_CURR | AI | TRUE
TM140220U001M1 | M | MCC | TM140220U001M1_RF | Pump#1 Mixing Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140220U001M1_RF | DI | TRUE
TM140220U001M1 | M | MCC | TM140220U001M1_RY | Pump#1 Mixing Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140220U001M1_RY | DI | TRUE
TM140220U001M1 | M | MCC | TM140220U001M1_STR | Pump#1 Mixing Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140220U001M1_STR | #N/A | #N/A
TM140220U002M1 | M | MCC | TM140220U002M1_CURR | Pump#2 Mixing Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140220U002M1_CURR | AI | TRUE
TM140220U002M1 | M | MCC | TM140220U002M1_RF | Pump#2 Mixing Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140220U002M1_RF | DI | TRUE
TM140220U002M1 | M | MCC | TM140220U002M1_RY | Pump#2 Mixing Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140220U002M1_RY | DI | TRUE
TM140220U002M1 | M | MCC | TM140220U002M1_STR | Pump#2 Mixing Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140220U002M1_STR | #N/A | #N/A
TM140220U003M1 | M | MCC | TM140220U003M1_CURR | Pump Sweetener | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140220U003M1_CURR | AI | TRUE
TM140220U003M1 | M | MCC | TM140220U003M1_RF | Pump Sweetener | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140220U003M1_RF | DI | TRUE
TM140220U003M1 | M | MCC | TM140220U003M1_RY | Pump Sweetener | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140220U003M1_RY | DI | TRUE
TM140220U003M1 | M | MCC | TM140220U003M1_STR | Pump Sweetener | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140220U003M1_STR | #N/A | #N/A
TM140220U004M1 | M | MCC | TM140220U004M1_CURR | Pump#1 Machine Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140220U004M1_CURR | AI | TRUE
TM140220U004M1 | M | MCC | TM140220U004M1_RF | Pump#1 Machine Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140220U004M1_RF | DI | TRUE
TM140220U004M1 | M | MCC | TM140220U004M1_RY | Pump#1 Machine Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140220U004M1_RY | DI | TRUE
TM140220U004M1 | M | MCC | TM140220U004M1_STR | Pump#1 Machine Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140220U004M1_STR | #N/A | #N/A
TM140220U005M1 | M | MCC | TM140220U005M1_CURR | Pump#2 Machine Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140220U005M1_CURR | AI | TRUE
TM140220U005M1 | M | MCC | TM140220U005M1_RF | Pump#2 Machine Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140220U005M1_RF | DI | TRUE
TM140220U005M1 | M | MCC | TM140220U005M1_RY | Pump#2 Machine Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140220U005M1_RY | DI | TRUE
TM140220U005M1 | M | MCC | TM140220U005M1_STR | Pump#2 Machine Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140220U005M1_STR | #N/A | #N/A
TM140220S001M1 | M | MCC | TM140220S001M1_CURR | 1.Stage Headbox Screen | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140220S001M1_CURR | AI | TRUE
TM140220S001M1 | M | MCC | TM140220S001M1_RF | 1.Stage Headbox Screen | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140220S001M1_RF | DI | TRUE
TM140220S001M1 | M | MCC | TM140220S001M1_RY | 1.Stage Headbox Screen | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140220S001M1_RY | DI | TRUE
TM140220S001M1 | M | MCC | TM140220S001M1_STR | 1.Stage Headbox Screen | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140220S001M1_STR | #N/A | #N/A
TM140220S002M1 | M | MCC | TM140220S002M1_CURR | 2.Stage Headbox Screen | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140220S002M1_CURR | AI | TRUE
TM140220S002M1 | M | MCC | TM140220S002M1_RF | 2.Stage Headbox Screen | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140220S002M1_RF | DI | TRUE
TM140220S002M1 | M | MCC | TM140220S002M1_RY | 2.Stage Headbox Screen | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140220S002M1_RY | DI | TRUE
TM140220S002M1 | M | MCC | TM140220S002M1_STR | 2.Stage Headbox Screen | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140220S002M1_STR | #N/A | #N/A
TM140220U006M1 | M | MCC | TM140220U006M1_CURR | Fan Pump | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140220U006M1_CURR | AI | TRUE
TM140220U006M1 | M | MCC | TM140220U006M1_RF | Fan Pump | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140220U006M1_RF | DI | TRUE
TM140220U006M1 | M | MCC | TM140220U006M1_RY | Fan Pump | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140220U006M1_RY | DI | TRUE
TM140220U006M1 | M | MCC | TM140220U006M1_STR | Fan Pump | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140220U006M1_STR | #N/A | #N/A
TM140220U007M1 | M | MCC | TM140220U007M1_CURR | Pump Wire Water Water Tank | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140220U007M1_CURR | AI | TRUE
TM140220U007M1 | M | MCC | TM140220U007M1_RF | Pump Wire Water Water Tank | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140220U007M1_RF | DI | TRUE
TM140220U007M1 | M | MCC | TM140220U007M1_RY | Pump Wire Water Water Tank | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140220U007M1_RY | DI | TRUE
TM140220U007M1 | M | MCC | TM140220U007M1_STR | Pump Wire Water Water Tank | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140220U007M1_STR | #N/A | #N/A
TM140221A005M1 | M | MCC | TM140221A005M1_CURR | Agitator Recovered Fiber Tank | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140221A005M1_CURR | AI | TRUE
TM140221A005M1 | M | MCC | TM140221A005M1_RF | Agitator Recovered Fiber Tank | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140221A005M1_RF | DI | TRUE
TM140221A005M1 | M | MCC | TM140221A005M1_RY | Agitator Recovered Fiber Tank | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140221A005M1_RY | DI | TRUE
TM140221A005M1 | M | MCC | TM140221A005M1_STR | Agitator Recovered Fiber Tank | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140221A005M1_STR | #N/A | #N/A
TM140221M001M1 | M | MCC | TM140221M001M1_CURR | Disc Filter | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140221M001M1_CURR | AI | TRUE
TM140221M001M1 | M | MCC | TM140221M001M1_RF | Disc Filter | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140221M001M1_RF | DI | TRUE
TM140221M001M1 | M | MCC | TM140221M001M1_RY | Disc Filter | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140221M001M1_RY | DI | TRUE
TM140221M001M1 | M | MCC | TM140221M001M1_STR | Disc Filter | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140221M001M1_STR | #N/A | #N/A
TM140221M001M2 | M | MCC | TM140221M001M2_CURR | Shower Oscillation Disc Filter | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140221M001M2_CURR | AI | TRUE
TM140221M001M2 | M | MCC | TM140221M001M2_RF | Shower Oscillation Disc Filter | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140221M001M2_RF | DI | TRUE
TM140221M001M2 | M | MCC | TM140221M001M2_RY | Shower Oscillation Disc Filter | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140221M001M2_RY | DI | TRUE
TM140221M001M2 | M | MCC | TM140221M001M2_STR | Shower Oscillation Disc Filter | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140221M001M2_STR | #N/A | #N/A
TM140221M001M3 | M | MCC | TM140221M001M3_CURR | Repulper Disc Filter | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140221M001M3_CURR | AI | TRUE
TM140221M001M3 | M | MCC | TM140221M001M3_RF | Repulper Disc Filter | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140221M001M3_RF | DI | TRUE
TM140221M001M3 | M | MCC | TM140221M001M3_RY | Repulper Disc Filter | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140221M001M3_RY | DI | TRUE
TM140221M001M3 | M | MCC | TM140221M001M3_STR | Repulper Disc Filter | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140221M001M3_STR | #N/A | #N/A
TM140221NE138 | M | MCC | TM140221NE138_RF | Cons.Trans. After Recovery Fibre Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140221NE138_RF | DI | TRUE
TM140221NE138 | M | MCC | TM140221NE138_RY | Cons.Trans. After Recovery Fibre Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140221NE138_RY | DI | TRUE
TM140221NE138 | M | MCC | TM140221NE138_STR | Cons.Trans. After Recovery Fibre Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140221NE138_STR | #N/A | #N/A
TM140221U001M1 | M | MCC | TM140221U001M1_CURR | Pump White Water | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140221U001M1_CURR | AI | TRUE
TM140221U001M1 | M | MCC | TM140221U001M1_RF | Pump White Water | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140221U001M1_RF | DI | TRUE
TM140221U001M1 | M | MCC | TM140221U001M1_RY | Pump White Water | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140221U001M1_RY | DI | TRUE
TM140221U001M1 | M | MCC | TM140221U001M1_STR | Pump White Water | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140221U001M1_STR | #N/A | #N/A
TM140221U002M1 | M | MCC | TM140221U002M1_CURR | Pump TM Area CRC | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140221U002M1_CURR | AI | TRUE
TM140221U002M1 | M | MCC | TM140221U002M1_RF | Pump TM Area CRC | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140221U002M1_RF | DI | TRUE
TM140221U002M1 | M | MCC | TM140221U002M1_RY | Pump TM Area CRC | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140221U002M1_RY | DI | TRUE
TM140221U002M1 | M | MCC | TM140221U002M1_STR | Pump TM Area CRC | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140221U002M1_STR | #N/A | #N/A
TM140221U003M1 | M | MCC | TM140221U003M1_CURR | Pump Yankee Pulping /Over flow | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140221U003M1_CURR | AI | TRUE
TM140221U003M1 | M | MCC | TM140221U003M1_RF | Pump Yankee Pulping /Over flow | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140221U003M1_RF | DI | TRUE
TM140221U003M1 | M | MCC | TM140221U003M1_RY | Pump Yankee Pulping /Over flow | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140221U003M1_RY | DI | TRUE
TM140221U003M1 | M | MCC | TM140221U003M1_STR | Pump Yankee Pulping /Over flow | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140221U003M1_STR | #N/A | #N/A
TM140221U004M1 | M | MCC | TM140221U004M1_CURR | Pump Recovered Fiber | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140221U004M1_CURR | AI | TRUE
TM140221U004M1 | M | MCC | TM140221U004M1_RF | Pump Recovered Fiber | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140221U004M1_RF | DI | TRUE
TM140221U004M1 | M | MCC | TM140221U004M1_RY | Pump Recovered Fiber | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140221U004M1_RY | DI | TRUE
TM140221U004M1 | M | MCC | TM140221U004M1_STR | Pump Recovered Fiber | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140221U004M1_STR | #N/A | #N/A
TM140221U005M1 | M | MCC | TM140221U005M1_CURR | Pump Cloudy Filtrate | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140221U005M1_CURR | AI | TRUE
TM140221U005M1 | M | MCC | TM140221U005M1_RF | Pump Cloudy Filtrate | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140221U005M1_RF | DI | TRUE
TM140221U005M1 | M | MCC | TM140221U005M1_RY | Pump Cloudy Filtrate | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140221U005M1_RY | DI | TRUE
TM140221U005M1 | M | MCC | TM140221U005M1_STR | Pump Cloudy Filtrate | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140221U005M1_STR | #N/A | #N/A
TM140221U006M1 | M | MCC | TM140221U006M1_CURR | Pump CWW HP Shower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140221U006M1_CURR | AI | TRUE
TM140221U006M1 | M | MCC | TM140221U006M1_RF | Pump CWW HP Shower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140221U006M1_RF | DI | TRUE
TM140221U006M1 | M | MCC | TM140221U006M1_RY | Pump CWW HP Shower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140221U006M1_RY | DI | TRUE
TM140221U006M1 | M | MCC | TM140221U006M1_STR | Pump CWW HP Shower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140221U006M1_STR | #N/A | #N/A
TM140221U007M1 | M | MCC | TM140221U007M1_CURR | Pump Clear Filtrate | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140221U007M1_CURR | AI | TRUE
TM140221U007M1 | M | MCC | TM140221U007M1_RF | Pump Clear Filtrate | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140221U007M1_RF | DI | TRUE
TM140221U007M1 | M | MCC | TM140221U007M1_RY | Pump Clear Filtrate | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140221U007M1_RY | DI | TRUE
TM140221U007M1 | M | MCC | TM140221U007M1_STR | Pump Clear Filtrate | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140221U007M1_STR | #N/A | #N/A
TM140221U008M1 | M | MCC | TM140221U008M1_CURR | Pump Disc Filter Shower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140221U008M1_CURR | AI | TRUE
TM140221U008M1 | M | MCC | TM140221U008M1_RF | Pump Disc Filter Shower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140221U008M1_RF | DI | TRUE
TM140221U008M1 | M | MCC | TM140221U008M1_RY | Pump Disc Filter Shower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140221U008M1_RY | DI | TRUE
TM140221U008M1 | M | MCC | TM140221U008M1_STR | Pump Disc Filter Shower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140221U008M1_STR | #N/A | #N/A
TM140221U009M1 | M | MCC | TM140221U009M1_CURR | Pump CWW LP Shower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140221U009M1_CURR | AI | TRUE
TM140221U009M1 | M | MCC | TM140221U009M1_RF | Pump CWW LP Shower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140221U009M1_RF | DI | TRUE
TM140221U009M1 | M | MCC | TM140221U009M1_RY | Pump CWW LP Shower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140221U009M1_RY | DI | TRUE
TM140221U009M1 | M | MCC | TM140221U009M1_STR | Pump CWW LP Shower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140221U009M1_STR | #N/A | #N/A
TM140221U011M1 | M | MCC | TM140221U011M1_CURR | Pump SCWW LP Shower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140221U011M1_CURR | AI | TRUE
TM140221U011M1 | M | MCC | TM140221U011M1_RF | Pump SCWW LP Shower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140221U011M1_RF | DI | TRUE
TM140221U011M1 | M | MCC | TM140221U011M1_RY | Pump SCWW LP Shower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140221U011M1_RY | DI | TRUE
TM140221U011M1 | M | MCC | TM140221U011M1_STR | Pump SCWW LP Shower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140221U011M1_STR | #N/A | #N/A
TM140221U012M1 | M | MCC | TM140221U012M1_CURR | Pump CWW Cleaning | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140221U012M1_CURR | AI | TRUE
TM140221U012M1 | M | MCC | TM140221U012M1_RF | Pump CWW Cleaning | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140221U012M1_RF | DI | TRUE
TM140221U012M1 | M | MCC | TM140221U012M1_RY | Pump CWW Cleaning | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140221U012M1_RY | DI | TRUE
TM140221U012M1 | M | MCC | TM140221U012M1_STR | Pump CWW Cleaning | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140221U012M1_STR | #N/A | #N/A
TM140221U013M1 | M | MCC | TM140221U013M1_CURR | Pump SCWW HP Shower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140221U013M1_CURR | AI | TRUE
TM140221U013M1 | M | MCC | TM140221U013M1_RF | Pump SCWW HP Shower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140221U013M1_RF | DI | TRUE
TM140221U013M1 | M | MCC | TM140221U013M1_RY | Pump SCWW HP Shower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140221U013M1_RY | DI | TRUE
TM140221U013M1 | M | MCC | TM140221U013M1_STR | Pump SCWW HP Shower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140221U013M1_STR | #N/A | #N/A
TM140317A001M1 | M | MCC | TM140317A001M1_CURR | Agitator Broke Deflaker Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140317A001M1_CURR | AI | TRUE
TM140317A001M1 | M | MCC | TM140317A001M1_RF | Agitator Broke Deflaker Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140317A001M1_RF | DI | TRUE
TM140317A001M1 | M | MCC | TM140317A001M1_RY | Agitator Broke Deflaker Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140317A001M1_RY | DI | TRUE
TM140317A001M1 | M | MCC | TM140317A001M1_STR | Agitator Broke Deflaker Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140317A001M1_STR | #N/A | #N/A
TM140317A002M1 | M | MCC | TM140317A002M1_CURR | Agitator Broke Thickened Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140317A002M1_CURR | AI | TRUE
TM140317A002M1 | M | MCC | TM140317A002M1_RF | Agitator Broke Thickened Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140317A002M1_RF | DI | TRUE
TM140317A002M1 | M | MCC | TM140317A002M1_RY | Agitator Broke Thickened Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140317A002M1_RY | DI | TRUE
TM140317A002M1 | M | MCC | TM140317A002M1_STR | Agitator Broke Thickened Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140317A002M1_STR | #N/A | #N/A
TM140317A003M1 | M | MCC | TM140317A003M1_CURR | Agitator Broke Interim Tower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140317A003M1_CURR | AI | TRUE
TM140317A003M1 | M | MCC | TM140317A003M1_RF | Agitator Broke Interim Tower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140317A003M1_RF | DI | TRUE
TM140317A003M1 | M | MCC | TM140317A003M1_RY | Agitator Broke Interim Tower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DO | Ready signal should be DI | _RY | TM140317A003M1_RY | DI | FALSE
TM140317A003M1 | M | MCC | TM140317A003M1_STR | Agitator Broke Interim Tower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140317A003M1_STR | #N/A | #N/A
TM140317M001M1 | M | MCC | TM140317M001M1_CURR | Deflaker | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140317M001M1_CURR | AI | TRUE
TM140317M001M1 | M | MCC | TM140317M001M1_RF | Deflaker | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140317M001M1_RF | DI | TRUE
TM140317M001M1 | M | MCC | TM140317M001M1_RY | Deflaker | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140317M001M1_RY | DI | TRUE
TM140317M001M1 | M | MCC | TM140317M001M1_STR | Deflaker | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140317M001M1_STR | #N/A | #N/A
TM140317M004M1 | M | MCC | TM140317M004M1_CURR | Agitator Yankee Pulper | ET | DCS | Actual Current | 0 | 130 | % | Profibus |  |  | BUS | AI |  | _CURR | TM140317M004M1_CURR | AI | TRUE
TM140317M004M1 | M | MCC | TM140317M004M1_RF | Agitator Yankee Pulper | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140317M004M1_RF | DI | TRUE
TM140317M004M1 | M | MCC | TM140317M004M1_RY | Agitator Yankee Pulper | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140317M004M1_RY | DI | TRUE
TM140317M004M1 | M | MCC | TM140317M004M1_STR | Agitator Yankee Pulper | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140317M004M1_STR | #N/A | #N/A
TM140317NE044 | M | MCC | TM140317NE044_RF | Cons.Trans. After Broke Deflaker Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140317NE044_RF | DI | TRUE
TM140317NE044 | M | MCC | TM140317NE044_RY | Cons.Trans. After Broke Deflaker Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140317NE044_RY | DI | TRUE
TM140317NE044 | M | MCC | TM140317NE044_STR | Cons.Trans. After Broke Deflaker Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140317NE044_STR | #N/A | #N/A
TM140317NE091 | M | MCC | TM140317NE091_RF | Cons.Trans. After Thickened Broke Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140317NE091_RF | DI | TRUE
TM140317NE091 | M | MCC | TM140317NE091_RY | Cons.Trans. After Thickened Broke Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140317NE091_RY | DI | TRUE
TM140317NE091 | M | MCC | TM140317NE091_STR | Cons.Trans. After Thickened Broke Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140317NE091_STR | #N/A | #N/A
TM140317U001M1 | M | MCC | TM140317U001M1_CURR | Pump Broke Deflaker Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140317U001M1_CURR | AI | TRUE
TM140317U001M1 | M | MCC | TM140317U001M1_RF | Pump Broke Deflaker Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140317U001M1_RF | DI | TRUE
TM140317U001M1 | M | MCC | TM140317U001M1_RY | Pump Broke Deflaker Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140317U001M1_RY | DI | TRUE
TM140317U001M1 | M | MCC | TM140317U001M1_STR | Pump Broke Deflaker Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140317U001M1_STR | #N/A | #N/A
TM140317U002M1 | M | MCC | TM140317U002M1_CURR | Pump Broke Thickened Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140317U002M1_CURR | AI | TRUE
TM140317U002M1 | M | MCC | TM140317U002M1_RF | Pump Broke Thickened Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140317U002M1_RF | DI | TRUE
TM140317U002M1 | M | MCC | TM140317U002M1_RY | Pump Broke Thickened Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140317U002M1_RY | DI | TRUE
TM140317U002M1 | M | MCC | TM140317U002M1_STR | Pump Broke Thickened Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140317U002M1_STR | #N/A | #N/A
TM140317U003M1 | M | MCC | TM140317U003M1_CURR | Pump 1 Broke Interim Tower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140317U003M1_CURR | AI | TRUE
TM140317U003M1 | M | MCC | TM140317U003M1_RF | Pump 1 Broke Interim Tower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140317U003M1_RF | DI | TRUE
TM140317U003M1 | M | MCC | TM140317U003M1_RY | Pump 1 Broke Interim Tower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140317U003M1_RY | DI | TRUE
TM140317U003M1 | M | MCC | TM140317U003M1_STR | Pump 1 Broke Interim Tower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140317U003M1_STR | #N/A | #N/A
TM140317U004M1 | M | MCC | TM140317U004M1_CURR | Pump 2 Broke Interim Tower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140317U004M1_CURR | AI | TRUE
TM140317U004M1 | M | MCC | TM140317U004M1_RF | Pump 2 Broke Interim Tower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140317U004M1_RF | DI | TRUE
TM140317U004M1 | M | MCC | TM140317U004M1_RY | Pump 2 Broke Interim Tower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140317U004M1_RY | DI | TRUE
TM140317U004M1 | M | MCC | TM140317U004M1_STR | Pump 2 Broke Interim Tower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140317U004M1_STR | #N/A | #N/A
TM140317U005M1 | M | MCC | TM140317U005M1_CURR | Pump Yankee Pulper | ET | DCS | Actual Current | 0 | 130 | % | Profibus |  |  | BUS | AI |  | _CURR | TM140317U005M1_CURR | AI | TRUE
TM140317U005M1 | M | MCC | TM140317U005M1_RF | Pump Yankee Pulper | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140317U005M1_RF | DI | TRUE
TM140317U005M1 | M | MCC | TM140317U005M1_RY | Pump Yankee Pulper | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140317U005M1_RY | DI | TRUE
TM140317U005M1 | M | MCC | TM140317U005M1_STR | Pump Yankee Pulper | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140317U005M1_STR | #N/A | #N/A
TM140317U006M1 | M | MCC | TM140317U006M1_CURR | Pump Yankee Pulper Recirculation | ET | DCS | Actual Current | 0 | 130 | % | Profibus |  |  | BUS | AI |  | _CURR | TM140317U006M1_CURR | AI | TRUE
TM140317U006M1 | M | MCC | TM140317U006M1_RF | Pump Yankee Pulper Recirculation | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140317U006M1_RF | DI | TRUE
TM140317U006M1 | M | MCC | TM140317U006M1_RY | Pump Yankee Pulper Recirculation | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140317U006M1_RY | DI | TRUE
TM140317U006M1 | M | MCC | TM140317U006M1_STR | Pump Yankee Pulper Recirculation | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140317U006M1_STR | #N/A | #N/A
TM140333F002M1 | M | MCC | TM140333F002M1_RF | Exhaust Fan Yankee Pulper | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140333F002M1_RF | DI | TRUE
TM140333F002M1 | M | MCC | TM140333F002M1_RY | Exhaust Fan Yankee Pulper | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DO | Ready signal should be DI | _RY | TM140333F002M1_RY | DI | FALSE
TM140333F002M1 | M | MCC | TM140333F002M1_STR | Exhaust Fan Yankee Pulper | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140333F002M1_STR | #N/A | #N/A
TM140320A001M1 | M | MCC | TM140320A001M1_CURR | Agitator Mixing Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140320A001M1_CURR | AI | TRUE
TM140320A001M1 | M | MCC | TM140320A001M1_RF | Agitator Mixing Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140320A001M1_RF | DI | TRUE
TM140320A001M1 | M | MCC | TM140320A001M1_RY | Agitator Mixing Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140320A001M1_RY | DI | TRUE
TM140320A001M1 | M | MCC | TM140320A001M1_STR | Agitator Mixing Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140320A001M1_STR | #N/A | #N/A
TM140320A002M1 | M | MCC | TM140320A002M1_CURR | Agitator Machine Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140320A002M1_CURR | AI | TRUE
TM140320A002M1 | M | MCC | TM140320A002M1_RF | Agitator Machine Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140320A002M1_RF | DI | TRUE
TM140320A002M1 | M | MCC | TM140320A002M1_RY | Agitator Machine Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140320A002M1_RY | DI | TRUE
TM140320A002M1 | M | MCC | TM140320A002M1_STR | Agitator Machine Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140320A002M1_STR | #N/A | #N/A
TM140320M001M1 | M | MCC | TM140320M001M1_CURR | Tickler Refiner TF-26 | ET | DCS | Actual Current | 0 | 120 | % | Profibus |  |  | BUS | AI |  | _CURR | TM140320M001M1_CURR | AI | TRUE
TM140320M001M1 | M | MCC | TM140320M001M1_FLT | Tickler Refiner TF-26 | K4 | DCS | Fault |  |  |  | Profibus |  |  | BUS | DI |  | _FLT | TM140320M001M1_FLT | DI | TRUE
TM140320M001M1 | M | MCC | TM140320M001M1_RY | Tickler Refiner TF-26 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140320M001M1_RY | DI | TRUE
TM140320M001M1 | M | MCC | TM140320M001M1_STR | Tickler Refiner TF-26 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140320M001M1_STR | #N/A | #N/A
TM140320M001M2 | M | MCC | TM140320M001M2_RF | Plate Adjustment Refiner | K1 | DCS | Run = 1 |  |  |  | Dry Contact | NO | 24 VDC | HW | DI |  | _RF | TM140320M001M2_RF | DI | TRUE
TM140320M001M2 | M | MCC | TM140320M001M2_RY | Plate Adjustment Refiner | K5 | DCS | Ready = 1 |  |  |  | Dry Contact | NO | 24 VDC | HW | DI |  | _RY | TM140320M001M2_RY | DI | TRUE
TM140320M001M2 | M | MCC | TM140320M001M2_STR | Plate Adjustment Refiner | K11 | DCS | Load Start |  |  |  | Dry Contact | NO | 24 VDC | HW | DO |  | _STR | TM140320M001M2_STR | #N/A | #N/A
TM140320M001M2 | M | MCC | TM140320M001M2_STR | Plate Adjustment Refiner | K12 | DCS | Release Start |  |  |  | Dry Contact | NO | 24 VDC | HW | DO |  | _STR | TM140320M001M2_STR | DO | TRUE
TM140320NE012 | M | MCC | TM140320NE012_RF | Cons.Trans. After P. Mixing Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140320NE012_RF | DI | TRUE
TM140320NE012 | M | MCC | TM140320NE012_RY | Cons.Trans. After P. Mixing Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140320NE012_RY | DI | TRUE
TM140320NE012 | M | MCC | TM140320NE012_STR | Cons.Trans. After P. Mixing Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140320NE012_STR | #N/A | #N/A
TM140320NE053 | M | MCC | TM140320NE053_RF | Cons.Trans. After P. Machine Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140320NE053_RF | DI | TRUE
TM140320NE053 | M | MCC | TM140320NE053_RY | Cons.Trans. After P. Machine Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140320NE053_RY | DI | TRUE
TM140320NE053 | M | MCC | TM140320NE053_STR | Cons.Trans. After P. Machine Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140320NE053_STR | #N/A | #N/A
TM140320U001M1 | M | MCC | TM140320U001M1_CURR | Pump#1 Mixing Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140320U001M1_CURR | AI | TRUE
TM140320U001M1 | M | MCC | TM140320U001M1_RF | Pump#1 Mixing Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140320U001M1_RF | DI | TRUE
TM140320U001M1 | M | MCC | TM140320U001M1_RY | Pump#1 Mixing Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140320U001M1_RY | DI | TRUE
TM140320U001M1 | M | MCC | TM140320U001M1_STR | Pump#1 Mixing Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140320U001M1_STR | #N/A | #N/A
TM140320U002M1 | M | MCC | TM140320U002M1_CURR | Pump#2 Mixing Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140320U002M1_CURR | AI | TRUE
TM140320U002M1 | M | MCC | TM140320U002M1_RF | Pump#2 Mixing Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140320U002M1_RF | DI | TRUE
TM140320U002M1 | M | MCC | TM140320U002M1_RY | Pump#2 Mixing Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140320U002M1_RY | DI | TRUE
TM140320U002M1 | M | MCC | TM140320U002M1_STR | Pump#2 Mixing Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140320U002M1_STR | #N/A | #N/A
TM140320U003M1 | M | MCC | TM140320U003M1_CURR | Pump Sweetener | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140320U003M1_CURR | AI | TRUE
TM140320U003M1 | M | MCC | TM140320U003M1_RF | Pump Sweetener | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140320U003M1_RF | DI | TRUE
TM140320U003M1 | M | MCC | TM140320U003M1_RY | Pump Sweetener | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140320U003M1_RY | DI | TRUE
TM140320U003M1 | M | MCC | TM140320U003M1_STR | Pump Sweetener | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140320U003M1_STR | #N/A | #N/A
TM140320U004M1 | M | MCC | TM140320U004M1_CURR | Pump#1 Machine Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140320U004M1_CURR | AI | TRUE
TM140320U004M1 | M | MCC | TM140320U004M1_RF | Pump#1 Machine Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140320U004M1_RF | DI | TRUE
TM140320U004M1 | M | MCC | TM140320U004M1_RY | Pump#1 Machine Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140320U004M1_RY | DI | TRUE
TM140320U004M1 | M | MCC | TM140320U004M1_STR | Pump#1 Machine Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140320U004M1_STR | #N/A | #N/A
TM140320U005M1 | M | MCC | TM140320U005M1_CURR | Pump#2 Machine Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140320U005M1_CURR | AI | TRUE
TM140320U005M1 | M | MCC | TM140320U005M1_RF | Pump#2 Machine Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140320U005M1_RF | DI | TRUE
TM140320U005M1 | M | MCC | TM140320U005M1_RY | Pump#2 Machine Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140320U005M1_RY | DI | TRUE
TM140320U005M1 | M | MCC | TM140320U005M1_STR | Pump#2 Machine Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140320U005M1_STR | #N/A | #N/A
TM140320S001M1 | M | MCC | TM140320S001M1_CURR | 1.Stage Headbox Screen | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140320S001M1_CURR | AI | TRUE
TM140320S001M1 | M | MCC | TM140320S001M1_RF | 1.Stage Headbox Screen | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140320S001M1_RF | DI | TRUE
TM140320S001M1 | M | MCC | TM140320S001M1_RY | 1.Stage Headbox Screen | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140320S001M1_RY | DI | TRUE
TM140320S001M1 | M | MCC | TM140320S001M1_STR | 1.Stage Headbox Screen | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140320S001M1_STR | #N/A | #N/A
TM140320S002M1 | M | MCC | TM140320S002M1_CURR | 2.Stage Headbox Screen | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140320S002M1_CURR | AI | TRUE
TM140320S002M1 | M | MCC | TM140320S002M1_RF | 2.Stage Headbox Screen | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140320S002M1_RF | DI | TRUE
TM140320S002M1 | M | MCC | TM140320S002M1_RY | 2.Stage Headbox Screen | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140320S002M1_RY | DI | TRUE
TM140320S002M1 | M | MCC | TM140320S002M1_STR | 2.Stage Headbox Screen | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140320S002M1_STR | #N/A | #N/A
TM140320U006M1 | M | MCC | TM140320U006M1_CURR | Fan Pump | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140320U006M1_CURR | AI | TRUE
TM140320U006M1 | M | MCC | TM140320U006M1_RF | Fan Pump | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140320U006M1_RF | DI | TRUE
TM140320U006M1 | M | MCC | TM140320U006M1_RY | Fan Pump | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140320U006M1_RY | DI | TRUE
TM140320U006M1 | M | MCC | TM140320U006M1_STR | Fan Pump | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140320U006M1_STR | #N/A | #N/A
TM140320U007M1 | M | MCC | TM140320U007M1_CURR | Pump Wire Water Water Tank | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140320U007M1_CURR | AI | TRUE
TM140320U007M1 | M | MCC | TM140320U007M1_RF | Pump Wire Water Water Tank | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140320U007M1_RF | DI | TRUE
TM140320U007M1 | M | MCC | TM140320U007M1_RY | Pump Wire Water Water Tank | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140320U007M1_RY | DI | TRUE
TM140320U007M1 | M | MCC | TM140320U007M1_STR | Pump Wire Water Water Tank | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140320U007M1_STR | #N/A | #N/A
TM140321A005M1 | M | MCC | TM140321A005M1_CURR | Agitator Recovered Fiber Tank | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140321A005M1_CURR | AI | TRUE
TM140321A005M1 | M | MCC | TM140321A005M1_RF | Agitator Recovered Fiber Tank | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140321A005M1_RF | DI | TRUE
TM140321A005M1 | M | MCC | TM140321A005M1_RY | Agitator Recovered Fiber Tank | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140321A005M1_RY | DI | TRUE
TM140321A005M1 | M | MCC | TM140321A005M1_STR | Agitator Recovered Fiber Tank | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140321A005M1_STR | #N/A | #N/A
TM140321M001M1 | M | MCC | TM140321M001M1_CURR | Disc Filter | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140321M001M1_CURR | AI | TRUE
TM140321M001M1 | M | MCC | TM140321M001M1_RF | Disc Filter | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140321M001M1_RF | DI | TRUE
TM140321M001M1 | M | MCC | TM140321M001M1_RY | Disc Filter | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140321M001M1_RY | DI | TRUE
TM140321M001M1 | M | MCC | TM140321M001M1_STR | Disc Filter | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140321M001M1_STR | #N/A | #N/A
TM140321M001M2 | M | MCC | TM140321M001M2_CURR | Shower Oscillation Disc Filter | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140321M001M2_CURR | AI | TRUE
TM140321M001M2 | M | MCC | TM140321M001M2_RF | Shower Oscillation Disc Filter | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140321M001M2_RF | DI | TRUE
TM140321M001M2 | M | MCC | TM140321M001M2_RY | Shower Oscillation Disc Filter | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140321M001M2_RY | DI | TRUE
TM140321M001M2 | M | MCC | TM140321M001M2_STR | Shower Oscillation Disc Filter | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140321M001M2_STR | #N/A | #N/A
TM140321M001M3 | M | MCC | TM140321M001M3_CURR | Repulper Disc Filter | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140321M001M3_CURR | AI | TRUE
TM140321M001M3 | M | MCC | TM140321M001M3_RF | Repulper Disc Filter | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140321M001M3_RF | DI | TRUE
TM140321M001M3 | M | MCC | TM140321M001M3_RY | Repulper Disc Filter | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140321M001M3_RY | DI | TRUE
TM140321M001M3 | M | MCC | TM140321M001M3_STR | Repulper Disc Filter | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140321M001M3_STR | #N/A | #N/A
TM140321NE138 | M | MCC | TM140321NE138_RF | Cons.Trans. After Recovery Fibre Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140321NE138_RF | DI | TRUE
TM140321NE138 | M | MCC | TM140321NE138_RY | Cons.Trans. After Recovery Fibre Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140321NE138_RY | DI | TRUE
TM140321NE138 | M | MCC | TM140321NE138_STR | Cons.Trans. After Recovery Fibre Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140321NE138_STR | #N/A | #N/A
TM140321U001M1 | M | MCC | TM140321U001M1_CURR | Pump White Water | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140321U001M1_CURR | AI | TRUE
TM140321U001M1 | M | MCC | TM140321U001M1_RF | Pump White Water | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140321U001M1_RF | DI | TRUE
TM140321U001M1 | M | MCC | TM140321U001M1_RY | Pump White Water | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140321U001M1_RY | DI | TRUE
TM140321U001M1 | M | MCC | TM140321U001M1_STR | Pump White Water | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140321U001M1_STR | #N/A | #N/A
TM140321U002M1 | M | MCC | TM140321U002M1_CURR | Pump TM Area CRC | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140321U002M1_CURR | AI | TRUE
TM140321U002M1 | M | MCC | TM140321U002M1_RF | Pump TM Area CRC | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140321U002M1_RF | DI | TRUE
TM140321U002M1 | M | MCC | TM140321U002M1_RY | Pump TM Area CRC | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140321U002M1_RY | DI | TRUE
TM140321U002M1 | M | MCC | TM140321U002M1_STR | Pump TM Area CRC | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140321U002M1_STR | #N/A | #N/A
TM140321U003M1 | M | MCC | TM140321U003M1_CURR | Pump Yankee Pulping /Over flow | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140321U003M1_CURR | AI | TRUE
TM140321U003M1 | M | MCC | TM140321U003M1_RF | Pump Yankee Pulping /Over flow | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140321U003M1_RF | DI | TRUE
TM140321U003M1 | M | MCC | TM140321U003M1_RY | Pump Yankee Pulping /Over flow | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140321U003M1_RY | DI | TRUE
TM140321U003M1 | M | MCC | TM140321U003M1_STR | Pump Yankee Pulping /Over flow | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140321U003M1_STR | #N/A | #N/A
TM140321U004M1 | M | MCC | TM140321U004M1_CURR | Pump Recovered Fiber | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140321U004M1_CURR | AI | TRUE
TM140321U004M1 | M | MCC | TM140321U004M1_RF | Pump Recovered Fiber | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140321U004M1_RF | DI | TRUE
TM140321U004M1 | M | MCC | TM140321U004M1_RY | Pump Recovered Fiber | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140321U004M1_RY | DI | TRUE
TM140321U004M1 | M | MCC | TM140321U004M1_STR | Pump Recovered Fiber | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140321U004M1_STR | #N/A | #N/A
TM140321U005M1 | M | MCC | TM140321U005M1_CURR | Pump Cloudy Filtrate | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140321U005M1_CURR | AI | TRUE
TM140321U005M1 | M | MCC | TM140321U005M1_RF | Pump Cloudy Filtrate | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140321U005M1_RF | DI | TRUE
TM140321U005M1 | M | MCC | TM140321U005M1_RY | Pump Cloudy Filtrate | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140321U005M1_RY | DI | TRUE
TM140321U005M1 | M | MCC | TM140321U005M1_STR | Pump Cloudy Filtrate | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140321U005M1_STR | #N/A | #N/A
TM140321U006M1 | M | MCC | TM140321U006M1_CURR | Pump CWW HP Shower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140321U006M1_CURR | AI | TRUE
TM140321U006M1 | M | MCC | TM140321U006M1_RF | Pump CWW HP Shower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140321U006M1_RF | DI | TRUE
TM140321U006M1 | M | MCC | TM140321U006M1_RY | Pump CWW HP Shower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140321U006M1_RY | DI | TRUE
TM140321U006M1 | M | MCC | TM140321U006M1_STR | Pump CWW HP Shower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140321U006M1_STR | #N/A | #N/A
TM140321U007M1 | M | MCC | TM140321U007M1_CURR | Pump Clear Filtrate | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140321U007M1_CURR | AI | TRUE
TM140321U007M1 | M | MCC | TM140321U007M1_RF | Pump Clear Filtrate | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140321U007M1_RF | DI | TRUE
TM140321U007M1 | M | MCC | TM140321U007M1_RY | Pump Clear Filtrate | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140321U007M1_RY | DI | TRUE
TM140321U007M1 | M | MCC | TM140321U007M1_STR | Pump Clear Filtrate | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140321U007M1_STR | #N/A | #N/A
TM140321U008M1 | M | MCC | TM140321U008M1_CURR | Pump Disc Filter Shower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140321U008M1_CURR | AI | TRUE
TM140321U008M1 | M | MCC | TM140321U008M1_RF | Pump Disc Filter Shower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140321U008M1_RF | DI | TRUE
TM140321U008M1 | M | MCC | TM140321U008M1_RY | Pump Disc Filter Shower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140321U008M1_RY | DI | TRUE
TM140321U008M1 | M | MCC | TM140321U008M1_STR | Pump Disc Filter Shower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140321U008M1_STR | #N/A | #N/A
TM140321U009M1 | M | MCC | TM140321U009M1_CURR | Pump CWW LP Shower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140321U009M1_CURR | AI | TRUE
TM140321U009M1 | M | MCC | TM140321U009M1_RF | Pump CWW LP Shower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140321U009M1_RF | DI | TRUE
TM140321U009M1 | M | MCC | TM140321U009M1_RY | Pump CWW LP Shower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140321U009M1_RY | DI | TRUE
TM140321U009M1 | M | MCC | TM140321U009M1_STR | Pump CWW LP Shower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140321U009M1_STR | #N/A | #N/A
TM140321U011M1 | M | MCC | TM140321U011M1_CURR | Pump SCWW LP Shower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140321U011M1_CURR | AI | TRUE
TM140321U011M1 | M | MCC | TM140321U011M1_RF | Pump SCWW LP Shower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140321U011M1_RF | DI | TRUE
TM140321U011M1 | M | MCC | TM140321U011M1_RY | Pump SCWW LP Shower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140321U011M1_RY | DI | TRUE
TM140321U011M1 | M | MCC | TM140321U011M1_STR | Pump SCWW LP Shower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140321U011M1_STR | #N/A | #N/A
TM140321U012M1 | M | MCC | TM140321U012M1_CURR | Pump CWW Cleaning | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140321U012M1_CURR | AI | TRUE
TM140321U012M1 | M | MCC | TM140321U012M1_RF | Pump CWW Cleaning | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140321U012M1_RF | DI | TRUE
TM140321U012M1 | M | MCC | TM140321U012M1_RY | Pump CWW Cleaning | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140321U012M1_RY | DI | TRUE
TM140321U012M1 | M | MCC | TM140321U012M1_STR | Pump CWW Cleaning | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140321U012M1_STR | #N/A | #N/A
TM140321U013M1 | M | MCC | TM140321U013M1_CURR | Pump SCWW HP Shower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140321U013M1_CURR | AI | TRUE
TM140321U013M1 | M | MCC | TM140321U013M1_RF | Pump SCWW HP Shower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140321U013M1_RF | DI | TRUE
TM140321U013M1 | M | MCC | TM140321U013M1_RY | Pump SCWW HP Shower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140321U013M1_RY | DI | TRUE
TM140321U013M1 | M | MCC | TM140321U013M1_STR | Pump SCWW HP Shower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140321U013M1_STR | #N/A | #N/A
TM140417A001M1 | M | MCC | TM140417A001M1_CURR | Agitator Broke Deflaker Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140417A001M1_CURR | AI | TRUE
TM140417A001M1 | M | MCC | TM140417A001M1_RF | Agitator Broke Deflaker Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140417A001M1_RF | DI | TRUE
TM140417A001M1 | M | MCC | TM140417A001M1_RY | Agitator Broke Deflaker Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140417A001M1_RY | DI | TRUE
TM140417A001M1 | M | MCC | TM140417A001M1_STR | Agitator Broke Deflaker Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140417A001M1_STR | #N/A | #N/A
TM140417A002M1 | M | MCC | TM140417A002M1_CURR | Agitator Broke Thickened Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140417A002M1_CURR | AI | TRUE
TM140417A002M1 | M | MCC | TM140417A002M1_RF | Agitator Broke Thickened Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140417A002M1_RF | DI | TRUE
TM140417A002M1 | M | MCC | TM140417A002M1_RY | Agitator Broke Thickened Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140417A002M1_RY | DI | TRUE
TM140417A002M1 | M | MCC | TM140417A002M1_STR | Agitator Broke Thickened Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140417A002M1_STR | #N/A | #N/A
TM140417A003M1 | M | MCC | TM140417A003M1_CURR | Agitator Broke Interim Tower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140417A003M1_CURR | AI | TRUE
TM140417A003M1 | M | MCC | TM140417A003M1_RF | Agitator Broke Interim Tower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140417A003M1_RF | DI | TRUE
TM140417A003M1 | M | MCC | TM140417A003M1_RY | Agitator Broke Interim Tower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DO | Ready signal should be DI | _RY | TM140417A003M1_RY | DI | FALSE
TM140417A003M1 | M | MCC | TM140417A003M1_STR | Agitator Broke Interim Tower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140417A003M1_STR | #N/A | #N/A
TM140417M001M1 | M | MCC | TM140417M001M1_CURR | Deflaker | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140417M001M1_CURR | AI | TRUE
TM140417M001M1 | M | MCC | TM140417M001M1_RF | Deflaker | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140417M001M1_RF | DI | TRUE
TM140417M001M1 | M | MCC | TM140417M001M1_RY | Deflaker | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140417M001M1_RY | DI | TRUE
TM140417M001M1 | M | MCC | TM140417M001M1_STR | Deflaker | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140417M001M1_STR | #N/A | #N/A
TM140417M004M1 | M | MCC | TM140417M004M1_CURR | Agitator Yankee Pulper | ET | DCS | Actual Current | 0 | 130 | % | Profibus |  |  | BUS | AI |  | _CURR | TM140417M004M1_CURR | AI | TRUE
TM140417M004M1 | M | MCC | TM140417M004M1_RF | Agitator Yankee Pulper | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140417M004M1_RF | DI | TRUE
TM140417M004M1 | M | MCC | TM140417M004M1_RY | Agitator Yankee Pulper | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140417M004M1_RY | DI | TRUE
TM140417M004M1 | M | MCC | TM140417M004M1_STR | Agitator Yankee Pulper | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140417M004M1_STR | #N/A | #N/A
TM140417NE044 | M | MCC | TM140417NE044_RF | Cons.Trans. After Broke Deflaker Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140417NE044_RF | DI | TRUE
TM140417NE044 | M | MCC | TM140417NE044_RY | Cons.Trans. After Broke Deflaker Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140417NE044_RY | DI | TRUE
TM140417NE044 | M | MCC | TM140417NE044_STR | Cons.Trans. After Broke Deflaker Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140417NE044_STR | #N/A | #N/A
TM140417NE091 | M | MCC | TM140417NE091_RF | Cons.Trans. After Thickened Broke Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140417NE091_RF | DI | TRUE
TM140417NE091 | M | MCC | TM140417NE091_RY | Cons.Trans. After Thickened Broke Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140417NE091_RY | DI | TRUE
TM140417NE091 | M | MCC | TM140417NE091_STR | Cons.Trans. After Thickened Broke Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140417NE091_STR | #N/A | #N/A
TM140417U001M1 | M | MCC | TM140417U001M1_CURR | Pump Broke Deflaker Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140417U001M1_CURR | AI | TRUE
TM140417U001M1 | M | MCC | TM140417U001M1_RF | Pump Broke Deflaker Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140417U001M1_RF | DI | TRUE
TM140417U001M1 | M | MCC | TM140417U001M1_RY | Pump Broke Deflaker Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140417U001M1_RY | DI | TRUE
TM140417U001M1 | M | MCC | TM140417U001M1_STR | Pump Broke Deflaker Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140417U001M1_STR | #N/A | #N/A
TM140417U002M1 | M | MCC | TM140417U002M1_CURR | Pump Broke Thickened Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140417U002M1_CURR | AI | TRUE
TM140417U002M1 | M | MCC | TM140417U002M1_RF | Pump Broke Thickened Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140417U002M1_RF | DI | TRUE
TM140417U002M1 | M | MCC | TM140417U002M1_RY | Pump Broke Thickened Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140417U002M1_RY | DI | TRUE
TM140417U002M1 | M | MCC | TM140417U002M1_STR | Pump Broke Thickened Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140417U002M1_STR | #N/A | #N/A
TM140417U003M1 | M | MCC | TM140417U003M1_CURR | Pump 1 Broke Interim Tower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140417U003M1_CURR | AI | TRUE
TM140417U003M1 | M | MCC | TM140417U003M1_RF | Pump 1 Broke Interim Tower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140417U003M1_RF | DI | TRUE
TM140417U003M1 | M | MCC | TM140417U003M1_RY | Pump 1 Broke Interim Tower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140417U003M1_RY | DI | TRUE
TM140417U003M1 | M | MCC | TM140417U003M1_STR | Pump 1 Broke Interim Tower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140417U003M1_STR | #N/A | #N/A
TM140417U005M1 | M | MCC | TM140417U005M1_CURR | Pump Yankee Pulper | ET | DCS | Actual Current | 0 | 130 | % | Profibus |  |  | BUS | AI |  | _CURR | TM140417U005M1_CURR | AI | TRUE
TM140417U005M1 | M | MCC | TM140417U005M1_RF | Pump Yankee Pulper | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140417U005M1_RF | DI | TRUE
TM140417U005M1 | M | MCC | TM140417U005M1_RY | Pump Yankee Pulper | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140417U005M1_RY | DI | TRUE
TM140417U005M1 | M | MCC | TM140417U005M1_STR | Pump Yankee Pulper | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140417U005M1_STR | #N/A | #N/A
TM140417U006M1 | M | MCC | TM140417U006M1_CURR | Pump Yankee Pulper Recirculation | ET | DCS | Actual Current | 0 | 130 | % | Profibus |  |  | BUS | AI |  | _CURR | TM140417U006M1_CURR | AI | TRUE
TM140417U006M1 | M | MCC | TM140417U006M1_RF | Pump Yankee Pulper Recirculation | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140417U006M1_RF | DI | TRUE
TM140417U006M1 | M | MCC | TM140417U006M1_RY | Pump Yankee Pulper Recirculation | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140417U006M1_RY | DI | TRUE
TM140417U006M1 | M | MCC | TM140417U006M1_STR | Pump Yankee Pulper Recirculation | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140417U006M1_STR | #N/A | #N/A
TM140433F002M1 | M | MCC | TM140433F002M1_RF | Exhaust Fan Yankee Pulper | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140433F002M1_RF | DI | TRUE
TM140433F002M1 | M | MCC | TM140433F002M1_RY | Exhaust Fan Yankee Pulper | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DO | Ready signal should be DI | _RY | TM140433F002M1_RY | DI | FALSE
TM140433F002M1 | M | MCC | TM140433F002M1_STR | Exhaust Fan Yankee Pulper | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140433F002M1_STR | #N/A | #N/A
TM140420A001M1 | M | MCC | TM140420A001M1_CURR | Agitator Mixing Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140420A001M1_CURR | AI | TRUE
TM140420A001M1 | M | MCC | TM140420A001M1_RF | Agitator Mixing Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140420A001M1_RF | DI | TRUE
TM140420A001M1 | M | MCC | TM140420A001M1_RY | Agitator Mixing Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140420A001M1_RY | DI | TRUE
TM140420A001M1 | M | MCC | TM140420A001M1_STR | Agitator Mixing Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140420A001M1_STR | #N/A | #N/A
TM140420A002M1 | M | MCC | TM140420A002M1_CURR | Agitator Machine Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140420A002M1_CURR | AI | TRUE
TM140420A002M1 | M | MCC | TM140420A002M1_RF | Agitator Machine Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140420A002M1_RF | DI | TRUE
TM140420A002M1 | M | MCC | TM140420A002M1_RY | Agitator Machine Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140420A002M1_RY | DI | TRUE
TM140420A002M1 | M | MCC | TM140420A002M1_STR | Agitator Machine Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140420A002M1_STR | #N/A | #N/A
TM140420M001M1 | M | MCC | TM140420M001M1_CURR | Tickler Refiner TF-26 | ET | DCS | Actual Current | 0 | 120 | % | Profibus |  |  | BUS | AI |  | _CURR | TM140420M001M1_CURR | AI | TRUE
TM140420M001M1 | M | MCC | TM140420M001M1_FLT | Tickler Refiner TF-26 | K4 | DCS | Fault |  |  |  | Profibus |  |  | BUS | DI |  | _FLT | TM140420M001M1_FLT | DI | TRUE
TM140420M001M1 | M | MCC | TM140420M001M1_RY | Tickler Refiner TF-26 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140420M001M1_RY | DI | TRUE
TM140420M001M1 | M | MCC | TM140420M001M1_STR | Tickler Refiner TF-26 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140420M001M1_STR | #N/A | #N/A
TM140420M001M2 | M | MCC | TM140420M001M2_RF | Plate Adjustment Refiner | K1 | DCS | Run = 1 |  |  |  | Dry Contact | NO | 24 VDC | HW | DI |  | _RF | TM140420M001M2_RF | DI | TRUE
TM140420M001M2 | M | MCC | TM140420M001M2_RY | Plate Adjustment Refiner | K5 | DCS | Ready = 1 |  |  |  | Dry Contact | NO | 24 VDC | HW | DI |  | _RY | TM140420M001M2_RY | DI | TRUE
TM140420M001M2 | M | MCC | TM140420M001M2_STR | Plate Adjustment Refiner | K11 | DCS | Load Start |  |  |  | Dry Contact | NO | 24 VDC | HW | DO |  | _STR | TM140420M001M2_STR | #N/A | #N/A
TM140420M001M2 | M | MCC | TM140420M001M2_STR | Plate Adjustment Refiner | K12 | DCS | Release Start |  |  |  | Dry Contact | NO | 24 VDC | HW | DO |  | _STR | TM140420M001M2_STR | DO | TRUE
TM140420NE012 | M | MCC | TM140420NE012_RF | Cons.Trans. After P. Mixing Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140420NE012_RF | DI | TRUE
TM140420NE012 | M | MCC | TM140420NE012_RY | Cons.Trans. After P. Mixing Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140420NE012_RY | DI | TRUE
TM140420NE012 | M | MCC | TM140420NE012_STR | Cons.Trans. After P. Mixing Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140420NE012_STR | #N/A | #N/A
TM140420NE053 | M | MCC | TM140420NE053_RF | Cons.Trans. After P. Machine Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140420NE053_RF | DI | TRUE
TM140420NE053 | M | MCC | TM140420NE053_RY | Cons.Trans. After P. Machine Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140420NE053_RY | DI | TRUE
TM140420NE053 | M | MCC | TM140420NE053_STR | Cons.Trans. After P. Machine Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140420NE053_STR | #N/A | #N/A
TM140420U001M1 | M | MCC | TM140420U001M1_CURR | Pump#1 Mixing Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140420U001M1_CURR | AI | TRUE
TM140420U001M1 | M | MCC | TM140420U001M1_RF | Pump#1 Mixing Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140420U001M1_RF | DI | TRUE
TM140420U001M1 | M | MCC | TM140420U001M1_RY | Pump#1 Mixing Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140420U001M1_RY | DI | TRUE
TM140420U001M1 | M | MCC | TM140420U001M1_STR | Pump#1 Mixing Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140420U001M1_STR | #N/A | #N/A
TM140420U002M1 | M | MCC | TM140420U002M1_CURR | Pump#2 Mixing Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140420U002M1_CURR | AI | TRUE
TM140420U002M1 | M | MCC | TM140420U002M1_RF | Pump#2 Mixing Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140420U002M1_RF | DI | TRUE
TM140420U002M1 | M | MCC | TM140420U002M1_RY | Pump#2 Mixing Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140420U002M1_RY | DI | TRUE
TM140420U002M1 | M | MCC | TM140420U002M1_STR | Pump#2 Mixing Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140420U002M1_STR | #N/A | #N/A
TM140420U003M1 | M | MCC | TM140420U003M1_CURR | Pump Sweetener | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140420U003M1_CURR | AI | TRUE
TM140420U003M1 | M | MCC | TM140420U003M1_RF | Pump Sweetener | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140420U003M1_RF | DI | TRUE
TM140420U003M1 | M | MCC | TM140420U003M1_RY | Pump Sweetener | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140420U003M1_RY | DI | TRUE
TM140420U003M1 | M | MCC | TM140420U003M1_STR | Pump Sweetener | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140420U003M1_STR | #N/A | #N/A
TM140420U004M1 | M | MCC | TM140420U004M1_CURR | Pump#1 Machine Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140420U004M1_CURR | AI | TRUE
TM140420U004M1 | M | MCC | TM140420U004M1_RF | Pump#1 Machine Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140420U004M1_RF | DI | TRUE
TM140420U004M1 | M | MCC | TM140420U004M1_RY | Pump#1 Machine Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140420U004M1_RY | DI | TRUE
TM140420U004M1 | M | MCC | TM140420U004M1_STR | Pump#1 Machine Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140420U004M1_STR | #N/A | #N/A
TM140420U005M1 | M | MCC | TM140420U005M1_CURR | Pump#2 Machine Chest | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140420U005M1_CURR | AI | TRUE
TM140420U005M1 | M | MCC | TM140420U005M1_RF | Pump#2 Machine Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140420U005M1_RF | DI | TRUE
TM140420U005M1 | M | MCC | TM140420U005M1_RY | Pump#2 Machine Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140420U005M1_RY | DI | TRUE
TM140420U005M1 | M | MCC | TM140420U005M1_STR | Pump#2 Machine Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140420U005M1_STR | #N/A | #N/A
TM140420S001M1 | M | MCC | TM140420S001M1_CURR | 1.Stage Headbox Screen | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140420S001M1_CURR | AI | TRUE
TM140420S001M1 | M | MCC | TM140420S001M1_RF | 1.Stage Headbox Screen | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140420S001M1_RF | DI | TRUE
TM140420S001M1 | M | MCC | TM140420S001M1_RY | 1.Stage Headbox Screen | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140420S001M1_RY | DI | TRUE
TM140420S001M1 | M | MCC | TM140420S001M1_STR | 1.Stage Headbox Screen | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140420S001M1_STR | #N/A | #N/A
TM140420S002M1 | M | MCC | TM140420S002M1_CURR | 2.Stage Headbox Screen | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140420S002M1_CURR | AI | TRUE
TM140420S002M1 | M | MCC | TM140420S002M1_RF | 2.Stage Headbox Screen | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140420S002M1_RF | DI | TRUE
TM140420S002M1 | M | MCC | TM140420S002M1_RY | 2.Stage Headbox Screen | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140420S002M1_RY | DI | TRUE
TM140420S002M1 | M | MCC | TM140420S002M1_STR | 2.Stage Headbox Screen | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140420S002M1_STR | #N/A | #N/A
TM140420U006M1 | M | MCC | TM140420U006M1_CURR | Fan Pump | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140420U006M1_CURR | AI | TRUE
TM140420U006M1 | M | MCC | TM140420U006M1_RF | Fan Pump | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140420U006M1_RF | DI | TRUE
TM140420U006M1 | M | MCC | TM140420U006M1_RY | Fan Pump | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140420U006M1_RY | DI | TRUE
TM140420U006M1 | M | MCC | TM140420U006M1_STR | Fan Pump | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140420U006M1_STR | #N/A | #N/A
TM140420U007M1 | M | MCC | TM140420U007M1_CURR | Pump Wire Water Water Tank | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140420U007M1_CURR | AI | TRUE
TM140420U007M1 | M | MCC | TM140420U007M1_RF | Pump Wire Water Water Tank | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140420U007M1_RF | DI | TRUE
TM140420U007M1 | M | MCC | TM140420U007M1_RY | Pump Wire Water Water Tank | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140420U007M1_RY | DI | TRUE
TM140420U007M1 | M | MCC | TM140420U007M1_STR | Pump Wire Water Water Tank | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140420U007M1_STR | #N/A | #N/A
TM140421A005M1 | M | MCC | TM140421A005M1_CURR | Agitator Recovered Fiber Tank | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140421A005M1_CURR | AI | TRUE
TM140421A005M1 | M | MCC | TM140421A005M1_RF | Agitator Recovered Fiber Tank | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140421A005M1_RF | DI | TRUE
TM140421A005M1 | M | MCC | TM140421A005M1_RY | Agitator Recovered Fiber Tank | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140421A005M1_RY | DI | TRUE
TM140421A005M1 | M | MCC | TM140421A005M1_STR | Agitator Recovered Fiber Tank | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140421A005M1_STR | #N/A | #N/A
TM140421M001M1 | M | MCC | TM140421M001M1_CURR | Disc Filter | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140421M001M1_CURR | AI | TRUE
TM140421M001M1 | M | MCC | TM140421M001M1_RF | Disc Filter | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140421M001M1_RF | DI | TRUE
TM140421M001M1 | M | MCC | TM140421M001M1_RY | Disc Filter | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140421M001M1_RY | DI | TRUE
TM140421M001M1 | M | MCC | TM140421M001M1_STR | Disc Filter | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140421M001M1_STR | #N/A | #N/A
TM140421M001M2 | M | MCC | TM140421M001M2_CURR | Shower Oscillation Disc Filter | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140421M001M2_CURR | AI | TRUE
TM140421M001M2 | M | MCC | TM140421M001M2_RF | Shower Oscillation Disc Filter | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140421M001M2_RF | DI | TRUE
TM140421M001M2 | M | MCC | TM140421M001M2_RY | Shower Oscillation Disc Filter | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140421M001M2_RY | DI | TRUE
TM140421M001M2 | M | MCC | TM140421M001M2_STR | Shower Oscillation Disc Filter | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140421M001M2_STR | #N/A | #N/A
TM140421M001M3 | M | MCC | TM140421M001M3_CURR | Repulper Disc Filter | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140421M001M3_CURR | AI | TRUE
TM140421M001M3 | M | MCC | TM140421M001M3_RF | Repulper Disc Filter | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140421M001M3_RF | DI | TRUE
TM140421M001M3 | M | MCC | TM140421M001M3_RY | Repulper Disc Filter | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140421M001M3_RY | DI | TRUE
TM140421M001M3 | M | MCC | TM140421M001M3_STR | Repulper Disc Filter | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140421M001M3_STR | #N/A | #N/A
TM140421NE138 | M | MCC | TM140421NE138_RF | Cons.Trans. After Recovery Fibre Chest | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140421NE138_RF | DI | TRUE
TM140421NE138 | M | MCC | TM140421NE138_RY | Cons.Trans. After Recovery Fibre Chest | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140421NE138_RY | DI | TRUE
TM140421NE138 | M | MCC | TM140421NE138_STR | Cons.Trans. After Recovery Fibre Chest | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140421NE138_STR | #N/A | #N/A
TM140421U001M1 | M | MCC | TM140421U001M1_CURR | Pump White Water | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140421U001M1_CURR | AI | TRUE
TM140421U001M1 | M | MCC | TM140421U001M1_RF | Pump White Water | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140421U001M1_RF | DI | TRUE
TM140421U001M1 | M | MCC | TM140421U001M1_RY | Pump White Water | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140421U001M1_RY | DI | TRUE
TM140421U001M1 | M | MCC | TM140421U001M1_STR | Pump White Water | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140421U001M1_STR | #N/A | #N/A
TM140421U002M1 | M | MCC | TM140421U002M1_CURR | Pump TM Area CRC | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140421U002M1_CURR | AI | TRUE
TM140421U002M1 | M | MCC | TM140421U002M1_RF | Pump TM Area CRC | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140421U002M1_RF | DI | TRUE
TM140421U002M1 | M | MCC | TM140421U002M1_RY | Pump TM Area CRC | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140421U002M1_RY | DI | TRUE
TM140421U002M1 | M | MCC | TM140421U002M1_STR | Pump TM Area CRC | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140421U002M1_STR | #N/A | #N/A
TM140421U003M1 | M | MCC | TM140421U003M1_CURR | Pump Yankee Pulping /Over flow | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140421U003M1_CURR | AI | TRUE
TM140421U003M1 | M | MCC | TM140421U003M1_RF | Pump Yankee Pulping /Over flow | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140421U003M1_RF | DI | TRUE
TM140421U003M1 | M | MCC | TM140421U003M1_RY | Pump Yankee Pulping /Over flow | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140421U003M1_RY | DI | TRUE
TM140421U003M1 | M | MCC | TM140421U003M1_STR | Pump Yankee Pulping /Over flow | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140421U003M1_STR | #N/A | #N/A
TM140421U004M1 | M | MCC | TM140421U004M1_CURR | Pump Recovered Fiber | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140421U004M1_CURR | AI | TRUE
TM140421U004M1 | M | MCC | TM140421U004M1_RF | Pump Recovered Fiber | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140421U004M1_RF | DI | TRUE
TM140421U004M1 | M | MCC | TM140421U004M1_RY | Pump Recovered Fiber | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140421U004M1_RY | DI | TRUE
TM140421U004M1 | M | MCC | TM140421U004M1_STR | Pump Recovered Fiber | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140421U004M1_STR | #N/A | #N/A
TM140421U005M1 | M | MCC | TM140421U005M1_CURR | Pump Cloudy Filtrate | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140421U005M1_CURR | AI | TRUE
TM140421U005M1 | M | MCC | TM140421U005M1_RF | Pump Cloudy Filtrate | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140421U005M1_RF | DI | TRUE
TM140421U005M1 | M | MCC | TM140421U005M1_RY | Pump Cloudy Filtrate | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140421U005M1_RY | DI | TRUE
TM140421U005M1 | M | MCC | TM140421U005M1_STR | Pump Cloudy Filtrate | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140421U005M1_STR | #N/A | #N/A
TM140421U006M1 | M | MCC | TM140421U006M1_CURR | Pump CWW HP Shower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140421U006M1_CURR | AI | TRUE
TM140421U006M1 | M | MCC | TM140421U006M1_RF | Pump CWW HP Shower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140421U006M1_RF | DI | TRUE
TM140421U006M1 | M | MCC | TM140421U006M1_RY | Pump CWW HP Shower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140421U006M1_RY | DI | TRUE
TM140421U006M1 | M | MCC | TM140421U006M1_STR | Pump CWW HP Shower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140421U006M1_STR | #N/A | #N/A
TM140421U007M1 | M | MCC | TM140421U007M1_CURR | Pump Clear Filtrate | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140421U007M1_CURR | AI | TRUE
TM140421U007M1 | M | MCC | TM140421U007M1_RF | Pump Clear Filtrate | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140421U007M1_RF | DI | TRUE
TM140421U007M1 | M | MCC | TM140421U007M1_RY | Pump Clear Filtrate | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140421U007M1_RY | DI | TRUE
TM140421U007M1 | M | MCC | TM140421U007M1_STR | Pump Clear Filtrate | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140421U007M1_STR | #N/A | #N/A
TM140421U008M1 | M | MCC | TM140421U008M1_CURR | Pump Disc Filter Shower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140421U008M1_CURR | AI | TRUE
TM140421U008M1 | M | MCC | TM140421U008M1_RF | Pump Disc Filter Shower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140421U008M1_RF | DI | TRUE
TM140421U008M1 | M | MCC | TM140421U008M1_RY | Pump Disc Filter Shower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140421U008M1_RY | DI | TRUE
TM140421U008M1 | M | MCC | TM140421U008M1_STR | Pump Disc Filter Shower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140421U008M1_STR | #N/A | #N/A
TM140421U009M1 | M | MCC | TM140421U009M1_CURR | Pump CWW LP Shower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140421U009M1_CURR | AI | TRUE
TM140421U009M1 | M | MCC | TM140421U009M1_RF | Pump CWW LP Shower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140421U009M1_RF | DI | TRUE
TM140421U009M1 | M | MCC | TM140421U009M1_RY | Pump CWW LP Shower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140421U009M1_RY | DI | TRUE
TM140421U009M1 | M | MCC | TM140421U009M1_STR | Pump CWW LP Shower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140421U009M1_STR | #N/A | #N/A
TM140421U011M1 | M | MCC | TM140421U011M1_CURR | Pump SCWW LP Shower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140421U011M1_CURR | AI | TRUE
TM140421U011M1 | M | MCC | TM140421U011M1_RF | Pump SCWW LP Shower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140421U011M1_RF | DI | TRUE
TM140421U011M1 | M | MCC | TM140421U011M1_RY | Pump SCWW LP Shower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140421U011M1_RY | DI | TRUE
TM140421U011M1 | M | MCC | TM140421U011M1_STR | Pump SCWW LP Shower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140421U011M1_STR | #N/A | #N/A
TM140421U012M1 | M | MCC | TM140421U012M1_CURR | Pump CWW Cleaning | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140421U012M1_CURR | AI | TRUE
TM140421U012M1 | M | MCC | TM140421U012M1_RF | Pump CWW Cleaning | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140421U012M1_RF | DI | TRUE
TM140421U012M1 | M | MCC | TM140421U012M1_RY | Pump CWW Cleaning | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140421U012M1_RY | DI | TRUE
TM140421U012M1 | M | MCC | TM140421U012M1_STR | Pump CWW Cleaning | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140421U012M1_STR | #N/A | #N/A
TM140421U013M1 | M | MCC | TM140421U013M1_CURR | Pump SCWW HP Shower | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140421U013M1_CURR | AI | TRUE
TM140421U013M1 | M | MCC | TM140421U013M1_RF | Pump SCWW HP Shower | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140421U013M1_RF | DI | TRUE
TM140421U013M1 | M | MCC | TM140421U013M1_RY | Pump SCWW HP Shower | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140421U013M1_RY | DI | TRUE
TM140421U013M1 | M | MCC | TM140421U013M1_STR | Pump SCWW HP Shower | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140421U013M1_STR | #N/A | #N/A
TM140517C001M1 | M | MCC | TM140517C001M1_CURR | Receiving and Feeding Conveyor | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140517C001M1_CURR | AI | TRUE
TM140517C001M1 | M | MCC | TM140517C001M1_RY | Receiving and Feeding Conveyor | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140517C001M1_RY | DI | TRUE
TM140517C001M1 | M | MCC | TM140517C001M1_STR | Receiving and Feeding Conveyor | K11 | DCS | Motor Start FWD |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140517C001M1_STR | #N/A | #N/A
TM140517C001M1 | M | MCC | TM140517C001M1_STR | Receiving and Feeding Conveyor | K12 | DCS | Motor Start REV |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140517C001M1_STR | DO | TRUE
TM140517M001M1 | M | MCC | TM140517M001M1_CURR | Converting Broke Pulper | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140517M001M1_CURR | AI | TRUE
TM140517M001M1 | M | MCC | TM140517M001M1_RF | Converting Broke Pulper | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140517M001M1_RF | DI | TRUE
TM140517M001M1 | M | MCC | TM140517M001M1_RY | Converting Broke Pulper | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140517M001M1_RY | DI | TRUE
TM140517M001M1 | M | MCC | TM140517M001M1_STR | Converting Broke Pulper | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140517M001M1_STR | #N/A | #N/A
TM140517T001M1 | M | MCC | TM140517T001M1_CURR | Air Separator 1 | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140517T001M1_CURR | AI | TRUE
TM140517T001M1 | M | MCC | TM140517T001M1_RF | Air Separator 1 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140517T001M1_RF | DI | TRUE
TM140517T001M1 | M | MCC | TM140517T001M1_RY | Air Separator 1 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140517T001M1_RY | DI | TRUE
TM140517T001M1 | M | MCC | TM140517T001M1_STR | Air Separator 1 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140517T001M1_STR | #N/A | #N/A
TM140517T002M1 | M | MCC | TM140517T002M1_CURR | Air Separator 2 | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140517T002M1_CURR | AI | TRUE
TM140517T002M1 | M | MCC | TM140517T002M1_RF | Air Separator 2 | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140517T002M1_RF | DI | TRUE
TM140517T002M1 | M | MCC | TM140517T002M1_RY | Air Separator 2 | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140517T002M1_RY | DI | TRUE
TM140517T002M1 | M | MCC | TM140517T002M1_STR | Air Separator 2 | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140517T002M1_STR | #N/A | #N/A
TM140517U001M1 | M | MCC | TM140517U001M1_CURR | Pump Pulper Discharge | ET | DCS | Actual Current |  |  |  | Profibus |  |  | BUS | AI |  | _CURR | TM140517U001M1_CURR | AI | TRUE
TM140517U001M1 | M | MCC | TM140517U001M1_RF | Pump Pulper Discharge | K1 | DCS | Run = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RF | TM140517U001M1_RF | DI | TRUE
TM140517U001M1 | M | MCC | TM140517U001M1_RY | Pump Pulper Discharge | K5 | DCS | Ready = 1 |  |  |  | Profibus |  |  | BUS | DI |  | _RY | TM140517U001M1_RY | DI | TRUE
TM140517U001M1 | M | MCC | TM140517U001M1_STR | Pump Pulper Discharge | K11 | DCS | Motor Start |  |  |  | Profibus |  |  | BUS | DO |  | _STR | TM140517U001M1_STR | #N/A | #N/A

## IO Summary
I/O COUNT SUMMARY
| AI | AO | DI | DO | TOTAL
SP2 DCS | 84 | 36 | 192 | 91 | 403
SP1 DCS | 1 | 0 | 0 | 1 | 2
SUM | 85 | 36 | 192 | 92 | 405

## Definitions
P&ID No. | The P&ID drawing number where the equipment is located.
Area | The Area where the equipment is located
Loop No. | Loop Number
Tag No. | Tag Name according to APP guideline
System Tag No. | Tag name to be appeared in DCS
Service Description | Process/service description
Signal Tag | Signal Tagname
Instrument Type | Type of instrument
Location | Location of the instrument
System | in DCS, PLC or local
IO Type | Type of input or output
Signal - Type | Signal type
Signal - Power | Power for the signal
Signal - Wire | wiring configuration
IO Loc. | Input and Output location
PV LO | Range Low
PV HI | Range High
Eng. Unit | Engineering Unit
Alarm | LLL- Low Low Low, HHH- High High High etc
State "0" | For Valves, If signal is zero, what willl be the valve opening.
State "1" | For Valves, If signal is one, what willl be the valve opening.
CV fail Action | For Valves, If air fails, what willl be the valve status.
CV Control Action | For Valves, Direction of the control.
PV CHAR | Process value characteristics
Rev | Revision
Supply By | Supplier name
Remarks

## Sheet1
’=FC P01
’=FC P02
’=FC S01
’=FC S02
’=FC S03
’=FC S05
’=101 S1
’=101 S2
’=103 S1
’=103 S2
’=105 S1
’=105 S2
’=FC S04
S11
S12
S9
S12.4
S10
S11.1