## CoverPage
SINAR MAS GROUP-APP INDONESIA
GPG DEPARTMENT
Customer : |  | PMPOLAND
Project : |  | OKI TM14.01
Area (see Note 1):
Dwg / Doc No (see Note 2): |  | P-OKITM07-300-06-LST-2001
Supplier doc. No. |  | PDZ-01216-091-52
Dwg / Doc Name : |  | Signal list
This issue : |  | 2021-05-12
Last issue : |  | 2021-05-12
Phase (see Note 3) : |  | 3
Purpose (see Note 4) : |  |  | `
Distribution :
Rev. | Date | Revision Notes
- | 2021-05-12 | ISSUED
Designed : | R. Krupa
Checked : | M. Obszański
Approved : | R. Krupa
Notes 1: | If the list contains all areas of the project, fill as "All Area". If it is for specific area of the project, fill the area name
Notes 2: | Refer to Document Numbering and Coding (GPG-100-01-PRO-0209)
Notes 3: | Phase: 1:Preliminary, 2: Final, 3: Issued for Construction, 4: As-Built
Notes 4: | Purpose: A:For Design ; B:For Information; C:For Approval; D:Approved for Construction; E:Preliminary; F:To be checked and returned
Notes 5: | Legend for Revision Code Column :
a) | The revision shall follow revision number from "A" onwards (A,B,C ..)
b) | If any row is modified or added, a revision no. shall be put in the "Rev" column.
c) | A revision note shall be put in the "Rev Code" column indicating the type of revision made as follows;
N = New Items that are added, M = Modified or Changed Items, D = Deleted Items
d) | The main "Revision" on the title block shall be changed accordingly to the latest revision no.
e) | The main "Date" of the revision shall be changed accordingly on the title block as well.
f) | If descriptions are needed to explain the revisions made, it should be put in the "Rev.Notes" column.
g) | All cells that are revised shall be COLOR-FILLED to indicate that it has been added modified.
Before a new revision, all previously color-filled cells to be REMOVED or UN-FILLED.
Yellow color to be used for color-filled cells.
h) | If any row of data is to be deleted, the row should be "Strikethrough". (E.g Deleted)
The row should be moved to the "Deleted" tab, where it will be kept there.
The row should not be deleted until it is sure that all the data in the row is not needed anymore.

## IO List
PMT: | [5 empty] | EPC: |  |  |  | Project No. | P-OKITM07 | [6 empty] | DCS I/O Database
[10 empty] | Project Name | OKITM Block 14
[10 empty] | Doc. No. | P-OKITM07-300-06-LST-2001 | [7 empty] | Abbreviations
Owner: | [5 empty] | Design Institute: |  |  |  | Rev. No. | 2 |  |  |  | Prep'd by | R. Krupa |  |  | EER Electronic Equipment Room |  |  |  | SQRT Square Root
[10 empty] | Purpose | REV |  |  |  | Chk'd by |  |  |  | CCR Control Center Room
[10 empty] | Date | 2021-04-13 |  |  |  | Appv'd by |  |  |  | ESP Electrostatic Precipitator
P&ID No. | Area |  | Loop No. | Suffix | Tag No. | DCS Tag Name | Process Area | Service Description | Signal Tag | Instrument Type | Location | System | IO Type | Signal |  |  | IO Loc. | PV LO | PV HI | Eng. Unit | Alarm | [6 empty] | State "0" | State "1" | CV Fail Action | CV Ctrl Action | PV CHAR | From |  | Cable |  |  | To |  | Rev. | Supply | Remarks
[14 empty] | Type | Power | Wire |  |  |  |  | LLL | LL | L | Nor. | H | HH | HHH | [5 empty] | JB/Panel No. | TB | Cable Number | Cable Type | Cable Order | Cabinet No. | TB |  | By
P-OKITM07-321-06-WRD-2007 | TM1401 | 30 | 642 |  | TM140130-PT-642 | TM140130PT642 | Wet End | TOTAL HEAD PRESSURE MEASUREMENT | PT | Pressure Transmitter | TM140130-SJB-001 | DCS | AI | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 0 | 500 | kPa
P-OKITM07-321-06-WRD-2001 | TM1401 | 30 | 665 |  | TM140130-ZI-665 | TM140130ZI665 | Wet End | HEADBOX SLICE LIP DISPLAY | ZI | Display | TM140130-CB-001 | DCS | AO | 4-20 mA | 24Vdc external | 4 | DCS Cabinet | 6 | 16 | mm
P-OKITM07-321-06-WRD-2006 | TM1401 | 30 | 665 |  | TM140130-GT-665 | TM140130GT665 | Wet End | HEADBOX SLICE LIP MEASUREMENT | GT | Limit Transmitter | TM140130-SJB-001 | DCS | AI | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 6 | 16 | mm
P-OKITM07-321-06-WRD-2006 | TM1401 | 30 | 665 |  | TM140130-GSO-665 | TM140130GSO665 | Wet End | HEADBOX SLICE LIP OPENED | GSO | Limit Switch Gap Headbox Open | TM140130-SJB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2006 | TM1401 | 30 | 665 |  | TM140130-GSC-665 | TM140130GSC665 | Wet End | HEADBOX SLICE LIP CLOSED | GSC | Limit Switch Gap Headbox Close | TM140130-SJB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2001 | TM1401 | 30 | 665 | A | TM140130-HS-665A | TM140130HS665A | Wet End | HEADBOX SLICE LIP OPEN CMD | HS | Push button | TM140130-CB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2001 | TM1401 | 30 | 665 | B | TM140130-HS-665B | TM140130HS665B | Wet End | HEADBOX SLICE LIP CLOSE CMD | HS | Push button | TM140130-CB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2006 | TM1401 | 30 | 665 |  | TM140130-CR-665 | TM140130CR665 | Wet End | HEADBOX SLICE LIP MEASUREMENT SERVICE ON | CR | Control relay | TM140130-SJB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2001 | TM1401 | 30 | 665 | A | TM140130-XL-665A | TM140130XL665A | Wet End | HEADBOX SLICE LIP OPENED IND | XL | Lamp | TM140130-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2001 | TM1401 | 30 | 665 | B | TM140130-XL-665B | TM140130XL665B | Wet End | HEADBOX SLICE LIP CLOSED IND | XL | Lamp | TM140130-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2007 | TM1401 | 30 | 670 |  | TM140130-SV-670 | TM140130SV670 | Wet End | HEADBOX VACUUM BREAKER OPEN/CLOSE | SV | Solenoid Valve | TM140130-SJB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2010 | TM1401 | 30 | 400 |  | TM140130-PS-400 | TM140130PS400 | Wet End | WET END AIR SUPPLY FRAME PRESSURE OK | PS | Pressure Switch | TM140130-SJB-002 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2003 | TM1401 | 30 | 417 |  | TM140130-PS-417 | TM140130PS417 | Wet End | WIRE GUIDE SUPPLY PRESSURE | PS | Pressure Switch | TM140130-CB-002 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2009 | TM1401 | 30 | 419 | A | TM140130-GE-419A | TM140130GE419A | Wet End | WIRE OVERTRAVEL FS ALARM | GE | Limit Switch Element | TM140130-JB-002 | DCS | DI | wet contact, NC | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2009 | TM1401 | 30 | 419 | B | TM140130-GE-419B | TM140130GE419B | Wet End | WIRE OVERTRAVEL FS STOP | GE | Limit Switch Element | TM140130-JB-002 | DCS | DI | wet contact, NC | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2009 | TM1401 | 30 | 419 | C | TM140130-GE-419C | TM140130GE419C | Wet End | WIRE OVERTRAVEL BS ALARM | GE | Limit Switch Element | TM140130-JB-002 | DCS | DI | wet contact, NC | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2009 | TM1401 | 30 | 419 | D | TM140130-GE-419D | TM140130GE419D | Wet End | WIRE OVERTRAVEL BS STOP | GE | Limit Switch Element | TM140130-JB-002 | DCS | DI | wet contact, NC | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2008 | TM1401 | 30 | 455 | A | TM140130-GE-455A | TM140130GE455A | Wet End | WIRE BREAST ROLL LIFT | GE | Limit Switch Element | TM140130-JB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2008 | TM1401 | 30 | 455 | B | TM140130-GE-455B | TM140130GE455B | Wet End | WIRE BREAST ROLL LOWER | GE | Limit Switch Element | TM140130-JB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2001 | TM1401 | 30 | 455 | A | TM140130-HS-455A | TM140130HS455A | Wet End | WIRE BREAST ROLL LIFT CMD | HS | Push button | TM140130-CB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2001 | TM1401 | 30 | 455 | B | TM140130-HS-455B | TM140130HS455B | Wet End | WIRE BREAST ROLL LOWER CMD | HS | Push button | TM140130-CB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2001 | TM1401 | 30 | 455 | A | TM140130-XL-455A | TM140130XL455A | Wet End | WIRE BREAST ROLL LIFT IND | XL | Lamp | TM140130-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2001 | TM1401 | 30 | 455 | B | TM140130-XL-455B | TM140130XL455B | Wet End | WIRE BREAST ROLL LOWER IND | XL | Lamp | TM140130-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2005 | TM1401 | 30 | 458 | _STR | TM140130M4258 | TM140130M458_STR | Wet End | WIRE HP SHOWER OSC. - ON/OFF | M | Start/Stop signal | TM140130-CB-005 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2005 | TM1401 | 30 | 458 | _RY | TM140130M4258 | TM140130M458_RY | Wet End | WIRE HP SHOWER OSC. - ALARM | M | Ready signal | TM140130-CB-005 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2005 | TM1401 | 30 | 458 | _RF | TM140130M4258 | TM140130M458_RF | Wet End | WIRE HP SHOWER OSC. - FEEDBACK | M | Feedback signal | TM140130-CB-005 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2005 | TM1401 | 30 | 458 | _SPC | TM140130M4258 | TM140130M458_SPC | Wet End | WIRE HP SHOWER OSC. - SPEED SP | M | Speed setpoint | TM140130-CB-005 | DCS | AO | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 0 | 1700 | mpm
P-OKITM07-321-06-WRD-2009 | TM1401 | 30 | 463 | A | TM140130-GE-463A | TM140130GE463A | Wet End | WIRE STRETCHER STRETCHING | GE | Limit Switch Element | TM140130-JB-002 | DCS | DI | wet contact, NC | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2009 | TM1401 | 30 | 463 | B | TM140130-GE-463B | TM140130GE463B | Wet End | WIRE STRETCHER LOOSENING | GE | Limit Switch Element | TM140130-JB-002 | DCS | DI | wet contact, NC | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2003 | TM1401 | 30 | 463 | A | TM140130-HS-463A | TM140130HS463A | Wet End | WIRE STRETCHER STRETCHING CMD | HS | Push button | TM140130-CB-002 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2003 | TM1401 | 30 | 463 | B | TM140130-HS-463B | TM140130HS463B | Wet End | WIRE STRETCHER LOOSENING CMD | HS | Push button | TM140130-CB-002 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2003 | TM1401 | 30 | 463 | C | TM140130-HS-463C | TM140130HS463C | Wet End | WIRE STRETCHER AUTO CMD | HS | Push button | TM140130-CB-002 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2003 | TM1401 | 30 | 463 | A | TM140130-XL-463A | TM140130XL463A | Wet End | WIRE STRETCHER STRETCHING IND | XL | Lamp | TM140130-CB-002 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2003 | TM1401 | 30 | 463 | B | TM140130-XL-463B | TM140130XL463B | Wet End | WIRE STRETCHER LOOSENING IND | XL | Lamp | TM140130-CB-002 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2003 | TM1401 | 30 | 463 | C | TM140130-XL-463C | TM140130XL463C | Wet End | WIRE STRETCHER AUTO CMD IND | XL | Lamp | TM140130-CB-002 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-321-06-WRD-2004 | TM1401 | 30 | 463 |  | TM140130-WI-463 | TM140130WI463 | Wet End | WIRE STRETCHER TENSION INDICATION | WI | Weight Indication | TM140130-CB-002 | DCS | AO | 4-20 mA | 24Vdc external | 4 | DCS Cabinet | 0 | 9 | kN/m
P-OKITM07-321-06-WRD-2008 | TM1401 | 30 | 463 |  | TM140130-WT-463 | TM140130WT463 | Wet End | WIRE STRETCHER TENSION | WT | Weight Transmitter | TM140130-JB-001 | DCS | AI | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 0 | 20 | kN
P-OKITM07-323-06-WRD-2006 | TM1401 | 30 | 316 | A | TM140130-GE-316A | TM140130GE316A | Wet End | PRESS LOADING CLOSE FS | GE | Limit Switch Element | TM140130-JB-103 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2008 | TM1401 | 30 | 316 | B | TM140130-GE-316B | TM140130GE316B | Wet End | PRESS LOADING CLOSE BS | GE | Limit Switch Element | TM140130-JB-203 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2006 | TM1401 | 30 | 316 | C | TM140130-GE-316C | TM140130GE316C | Wet End | PRESS LOADING UNLOAD FS | GE | Limit Switch Element | TM140130-JB-103 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2008 | TM1401 | 30 | 316 | D | TM140130-GE-316D | TM140130GE316D | Wet End | PRESS LOADING UNLOAD BS | GE | Limit Switch Element | TM140130-JB-203 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2003 | TM1401 | 30 | 270 |  | TM140130-PS-270 | TM140130PS270 | Wet End | SPR CONTROL BOX PRESSURE OK | PS | Pressure Switch | TM140130-CB-004 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2006 | TM1401 | 30 | 315 |  | TM140130-FS-315 | TM140130FS315 | Wet End | SPR SUCTION BOX SEALING WATER FLOW SWITCH | FS | Flow Safety | TM140130-JB-103 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2003 | TM1401 | 30 | 316 | A | TM140130-HS-316A | TM140130HS316A | Wet End | PRESS LOADING CLOSE CMD | HS | Push button | TM140130-CB-004 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2003 | TM1401 | 30 | 316 | B | TM140130-HS-316B | TM140130HS316B | Wet End | PRESS LOADING OPEN CMD | HS | Push button | TM140130-CB-004 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2003 | TM1401 | 30 | 316 | C | TM140130-HS-316C | TM140130HS316C | Wet End | PRESS LOADING LOAD CMD | HS | Push button | TM140130-CB-004 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2003 | TM1401 | 30 | 316 | A | TM140130-XL-316A | TM140130XL316A | Wet End | PRESS LOADING CLOSE IND | XL | Lamp | TM140130-CB-004 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2003 | TM1401 | 30 | 316 | B | TM140130-XL-316B | TM140130XL316B | Wet End | PRESS LOADING OPEN IND | XL | Lamp | TM140130-CB-004 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2003 | TM1401 | 30 | 316 | C | TM140130-XL-316C | TM140130XL316C | Wet End | PRESS LOADING LOAD IND | XL | Lamp | TM140130-CB-004 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2001 | TM1401 | 30 | 317 |  | TM140130-PS-317 | TM140130PS317 | Wet End | FELT AUTO GUIDE SUPPLY PRESSURE | PS | Pressure Switch | TM140130-CB-003 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2028 | TM1401 | 30 | 318 |  | TM140130-SV-318 | TM140130SV318 | Wet End | UTM CHUTE BLOWER ON/OFF | SV | Solenoid Valve | TM140131-SJB-002 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2005 | TM1401 | 30 | 319 | A | TM140130-GE-319A | TM140130GE319A | Wet End | FELT OVERTRAVEL FS ALARM | GE | Limit Switch Element | TM140130-JB-003 | DCS | DI | wet contact, NC | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2005 | TM1401 | 30 | 319 | B | TM140130-GE-319B | TM140130GE319B | Wet End | FELT OVERTRAVEL FS STOP | GE | Limit Switch Element | TM140130-JB-003 | DCS | DI | wet contact, NC | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2011 | TM1401 | 30 | 319 | C | TM140130-GE-319C | TM140130GE319C | Wet End | FELT OVERTRAVEL BS ALARM | GE | Limit Switch Element | TM140130-JB-403 | DCS | DI | wet contact, NC | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2011 | TM1401 | 30 | 319 | D | TM140130-GE-319D | TM140130GE319D | Wet End | FELT OVERTRAVEL BS STOP | GE | Limit Switch Element | TM140130-JB-403 | DCS | DI | wet contact, NC | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2011 | TM1401 | 30 | 350 | A | TM140130-GE-350A | TM140130GE350A | Wet End | FELT STRETCHER STRETCHING | GE | Limit Switch Element | TM140130-JB-403 | DCS | DI | wet contact, NC | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2011 | TM1401 | 30 | 350 | B | TM140130-GE-350B | TM140130GE350B | Wet End | FELT STRETCHER LOOSENING | GE | Limit Switch Element | TM140130-JB-403 | DCS | DI | wet contact, NC | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2011 | TM1401 | 30 | 350 | C | TM140130-GE-350C | TM140130GE350C | Wet End | FELT STRETCHER SHAFT OK | GE | Limit Switch Element | TM140130-JB-403 | DCS | DI | wet contact, NC | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2001 | TM1401 | 30 | 350 | A | TM140130-HS-350A | TM140130HS350A | Wet End | FELT STRETCHER STRETCHING CMD | HS | Push button | TM140130-CB-003 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2001 | TM1401 | 30 | 350 | B | TM140130-HS-350B | TM140130HS350B | Wet End | FELT STRETCHER LOOSENING CMD | HS | Push button | TM140130-CB-003 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2001 | TM1401 | 30 | 350 | C | TM140130-HS-350C | TM140130HS350C | Wet End | FELT STRETCHER AUTO CMD | HS | Push button | TM140130-CB-003 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2001 | TM1401 | 30 | 350 | A | TM140130-XL-350A | TM140130XL350A | Wet End | FELT STRETCHER STRETCHING IND | XL | Lamp | TM140130-CB-003 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2001 | TM1401 | 30 | 350 | B | TM140130-XL-350B | TM140130XL350B | Wet End | FELT STRETCHER LOOSENING IND | XL | Lamp | TM140130-CB-003 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2001 | TM1401 | 30 | 350 | C | TM140130-XL-350C | TM140130XL350C | Wet End | FELT STRETCHER AUTO IND | XL | Lamp | TM140130-CB-003 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2002 | TM1401 | 30 | 350 |  | TM140130-WI-350 | TM140130WI350 | Wet End | FELT STRETCHER TENSION INDICATION | WI | Weight Indication | TM140130-CB-003 | DCS | AO | 4-20 mA | 24Vdc external | 4 | DCS Cabinet | 0 | 6.25 | kN/m
P-OKITM07-323-06-WRD-2011 | TM1401 | 30 | 350 |  | TM140130-WT-350 | TM140130WT350 | Wet End | FELT STRETCHER TENSION MEASUREMENT | WT | Weight Transmitter | TM140130-JB-403 | DCS | AI | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 0 | 20 | kN
P-OKITM07-323-06-WRD-2004 | TM1401 | 30 | 354 | _STR | TM140130M0354 | TM140130M354_STR | Wet End | FELT HP SHOWER OSC. - ON/OFF | M | Start/Stop signal | TM140130-CB-006 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2004 | TM1401 | 30 | 354 | _RY | TM140130M0354 | TM140130M354_RY | Wet End | FELT HP SHOWER OSC. - ALARM | M | Ready signal | TM140130-CB-006 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2004 | TM1401 | 30 | 354 | _RF | TM140130M0354 | TM140130M354_RF | Wet End | FELT HP SHOWER OSC. - FEEDBACK | M | Feedback signal | TM140130-CB-006 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2004 | TM1401 | 30 | 354 | _SPC | TM140130M0354 | TM140130M354_SPC | Wet End | FELT HP SHOWER OSC. - SPPED SP | M | Speed setpoint | TM140130-CB-006 | DCS | AO | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 0 | 1700 | mpm
P-OKITM07-323-06-WRD-2012 | TM1401 | 31 | 200 |  | TM140131-PS-200 | TM140131PS200 | Dry End | YANKEE DOCTORS CTRL. BOX | PS | Pressure Switch | TM140131-CB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2006 | TM1401 | 31 | 210 |  | TM140131-GE-210 | TM140131GE210 | Dry End | YANKEE DRYER CLEANING DOCTOR LOADED | GE | Limit Switch Element | TM140130-JB-103 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2012 | TM1401 | 31 | 210 | A | TM140131-HS-210A | TM140131HS210A | Dry End | YANKEE DRYER CLEANING DOCTOR LOAD CMD | HS | Push button | TM140131-CB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2012 | TM1401 | 31 | 210 | B | TM140131-HS-210B | TM140131HS210B | Dry End | YANKEE DRYER CLEANING DOCTOR UNLOAD CMD | HS | Push button | TM140131-CB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2014 | TM1401 | 31 | 210 | A | TM140131-XL-210A | TM140131XL210A | Dry End | YANKEE DRYER CLEANING DOCTOR LOADED IND | XL | Lamp | TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2014 | TM1401 | 31 | 210 | B | TM140131-XL-210B | TM140131XL210B | Dry End | YANKEE DRYER CLEANING DOCTOR UNLOAD IND | XL | Lamp | TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2015 | TM1401 | 31 | 210 | A | TM140131-SV-210A | TM140131SV210A | Dry End | YANKEE DRYER CLEANING DOCTOR LOAD | SV | Solenoid Valve | TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2015 | TM1401 | 31 | 210 | B | TM140131-SV-210B | TM140131SV210B | Dry End | YANKEE DRYER CLEANING DOCTOR UNLOAD | SV | Solenoid Valve | TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2012 | TM1401 | 31 | 211 |  | TM140131-HS-211 | TM140131HS211 | Dry End | YANKEE DRYER CLEANING DOCTOR TOUCH CMD | HS | Push button | TM140131-CB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2014 | TM1401 | 31 | 211 |  | TM140131-XL-211 | TM140131XL211 | Dry End | YANKEE DRYER CLEANING DOCTOR TOUCH IND | XL | Lamp | TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2015 | TM1401 | 31 | 211 |  | TM140131-SV-211 | TM140131SV211 | Dry End | YANKEE DRYER CLEANING DOCTOR TOUCH | SV | Solenoid Valve | TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2008 | TM1401 | 31 | 215 |  | TM140131-GE-215 | TM140131GE215 | Dry End | YANKEE DRYER CLEANING DOCTOR OSCILLATED | GE | Limit Switch Element | TM140130-JB-203 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2006 | TM1401 | 31 | 220 |  | TM140131-GE-220 | TM140131GE220 | Dry End | YANKEE DRYER CREPING DOCTOR LOADED | GE | Limit Switch Element | TM140130-JB-103 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2012 | TM1401 | 31 | 220 | A | TM140131-HS-220A | TM140131HS220A | Dry End | YANKEE DRYER CREPING DOCTOR LOAD CMD | HS | Push button | TM140131-CB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2012 | TM1401 | 31 | 220 | B | TM140131-HS-220B | TM140131HS220B | Dry End | YANKEE DRYER CREPING DOCTOR UNLOAD CMD | HS | Push button | TM140131-CB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2014 | TM1401 | 31 | 220 | A | TM140131-XL-220A | TM140131XL220A | Dry End | YANKEE DRYER CREPING DOCTOR LOADED IND | XL | Lamp | TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2014 | TM1401 | 31 | 220 | B | TM140131-XL-220B | TM140131XL220B | Dry End | YANKEE DRYER CREPING DOCTOR UNLOADED IND | XL | Lamp | TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2016 | TM1401 | 31 | 220 | A | TM140131-SV-220A | TM140131SV220A | Dry End | YANKEE DRYER CREPING DOCTOR LOAD | SV | Solenoid Valve | TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2016 | TM1401 | 31 | 220 | B | TM140131-SV-220B | TM140131SV220B | Dry End | YANKEE DRYER CREPING DOCTOR UNLOAD | SV | Solenoid Valve | TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2012 | TM1401 | 31 | 221 |  | TM140131-HS-221 | TM140131HS221 | Dry End | YANKEE DRYER CREPING DOCTOR SERVICE CMD | HS | Push button | TM140131-CB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2014 | TM1401 | 31 | 221 |  | TM140131-XL-221 | TM140131XL221 | Dry End | YANKEE DRYER CREPING DOCTOR SERVICED IND | XL | Lamp | TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2016 | TM1401 | 31 | 221 | A | TM140131-SV-221A | TM140131SV221A | Dry End | YANKEE DRYER CREPING DOCTOR SERVICE ON | SV | Solenoid Valve | TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2016 | TM1401 | 31 | 221 | B | TM140131-SV-221B | TM140131SV221B | Dry End | YANKEE DRYER CREPING DOCTOR SERVICE OFF | SV | Solenoid Valve | TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2008 | TM1401 | 31 | 225 |  | TM140131-GE-225 | TM140131GE225 | Dry End | YANKEE DRYER CREPING DOCTOR OSCILLATED | GE | Limit Switch Element | TM140130-JB-203 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2006 | TM1401 | 31 | 230 |  | TM140131-GE-230 | TM140131GE230 | Dry End | YANKEE DRYER CUT-OFF DOCTOR LOADED | GE | Limit Switch Element | TM140130-JB-103 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2013 | TM1401 | 31 | 230 | A | TM140131-HS-230A | TM140131HS230A | Dry End | YANKEE DRYER CUT-OFF DOCTOR LOAD CMD | HS | Push button | TM140131-CB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2013 | TM1401 | 31 | 230 | B | TM140131-HS-230B | TM140131HS230B | Dry End | YANKEE DRYER CUT-OFF DOCTOR UNLOAD CMD | HS | Push button | TM140131-CB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2014 | TM1401 | 31 | 230 | A | TM140131-XL-230A | TM140131XL230A | Dry End | YANKEE DRYER CUT-OFF DOCTOR LOADED IND | XL | Lamp | TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2014 | TM1401 | 31 | 230 | B | TM140131-XL-230B | TM140131XL230B | Dry End | YANKEE DRYER CUT-OFF DOCTOR UNLOAD IND | XL | Lamp | TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2016 | TM1401 | 31 | 230 | A | TM140131-SV-230A | TM140131SV230A | Dry End | YANKEE DRYER CUT-OFF DOCTOR LOAD | SV | Solenoid Valve | TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2016 | TM1401 | 31 | 230 | B | TM140131-SV-230B | TM140131SV230B | Dry End | YANKEE DRYER CUT-OFF DOCTOR UNLOAD | SV | Solenoid Valve | TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2013 | TM1401 | 31 | 231 |  | TM140131-HS-231 | TM140131HS231 | Dry End | YANKEE DRYER CUT-OFF DOCTOR SERVICE CMD | HS | Push button | TM140131-CB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2015 | TM1401 | 31 | 231 |  | TM140131-XL-231 | TM140131XL231 | Dry End | YANKEE DRYER CUT-OFF DOCTOR SERVICED IND | XL | Lamp | TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2016 | TM1401 | 31 | 231 | A | TM140131-SV-231A | TM140131SV231A | Dry End | YANKEE DRYER CUT-OFF DOCTOR SERVICE ON | SV | Solenoid Valve | TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2016 | TM1401 | 31 | 231 | B | TM140131-SV-231B | TM140131SV231B | Dry End | YANKEE DRYER CUT-OFF DOCTOR SERVICE OFF | SV | Solenoid Valve | TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2008 | TM1401 | 31 | 235 |  | TM140131-GE-235 | TM140131GE235 | Dry End | YANKEE DRYER CUT-OFF DOCTOR OSCILLATED | GE | Limit Switch Element | TM140130-JB-203 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2020 | TM1401 | 31 | 600 |  | TM140131-PS-600 | TM140131PS600 | Dry End | CABINET TM140131-SJB-001 | PS | Pressure Switch | TM140131-SJB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2001 | TM1401 | 31 | 601 | A | TM140131-HS-601A | TM140131HS601A | Dry End | REEL RUN AUTO CMD | HS | Push button | TM140131-CP-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2001 | TM1401 | 31 | 601 | B | TM140131-HS-601B | TM140131HS601B | Dry End | REEL RUN STOP CMD | HS | Push button | TM140131-CP-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2005 | TM1401 | 31 | 601 | A | TM140131-XL-601A | TM140131XL601A | Dry End | REEL RUN AUTO IND | XL | Lamp | TM140131-CP-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2005 | TM1401 | 31 | 601 | B | TM140131-XL-601B | TM140131XL601B | Dry End | REEL RUN STOP IND | XL | Lamp | TM140131-CP-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2005 | TM1401 | 31 | 601 | C | TM140131-XL-601C | TM140131XL601C | Dry End | REEL RUN MANUAL IND | XL | Lamp | TM140131-CP-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2026 | TM1401 | 31 | 602 | A | TM140131-XL-602 | TM140131XL602A | Dry End | POPE REEL SIGNAL TOWER - RED | XL | Lamp | TM140131-SJB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2026 | TM1401 | 31 | 602 | B | TM140131-XL-602 | TM140131XL602B | Dry End | POPE REEL SIGNAL TOWER - YELLOW | XL | Lamp | TM140131-SJB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2026 | TM1401 | 31 | 602 | C | TM140131-XL-602 | TM140131XL602C | Dry End | POPE REEL SIGNAL TOWER - BLUE | XL | Lamp | TM140131-SJB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2026 | TM1401 | 31 | 602 |  | TM140131-XL-602 | TM140131XA602 | Dry End | POPE REEL SIGNAL TOWER - HORN | XA | Horn | TM140131-SJB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2015 | TM1401 | 31 | 605 | A | TM140131-GE-605A | TM140131GE605A_NO | Dry End | POPE REEL FRAMEWORK GATE CLOSED FS | GE | Limit Switch Element | TM140131-JB-460 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2015 | TM1401 | 31 | 605 | A | TM140131-GE-605A | TM140131GE605A_NC | Dry End | POPE REEL FRAMEWORK GATE CLOSED FS | GE | Limit Switch Element | TM140131-JB-460 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2019 | TM1401 | 31 | 605 | B | TM140131-GE-605B | TM140131GE605B_NO | Dry End | POPE REEL FRAMEWORK GATE CLOSED BS | GE | Limit Switch Element | TM140131-JB-860 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2019 | TM1401 | 31 | 605 | B | TM140131-GE-605B | TM140131GE605B_NC | Dry End | POPE REEL FRAMEWORK GATE CLOSED BS | GE | Limit Switch Element | TM140131-JB-860 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2001 | TM1401 | 31 | 605 | A | TM140131-HS-605A | TM140131HS605A | Dry End | POPE REEL FRAMEWORK GATE OPEN CMD | HS | Push button | TM140131-CP-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2001 | TM1401 | 31 | 605 | B | TM140131-HS-605B | TM140131HS605B | Dry End | POPE REEL FRAMEWORK GATE CLOSE CMD | HS | Push button | TM140131-CP-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2005 | TM1401 | 31 | 605 | A | TM140131-XL-605A | TM140131XL605A | Dry End | POPE REEL FRAMEWORK GATE OPEN IND | XL | Lamp | TM140131-CP-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2021 | TM1401 | 31 | 605 | A | TM140131-SV-605A | TM140131SV605A | Dry End | POPE REEL FRAMEWORK GATE OPEN | SV | Solenoid Valve | TM140131-SJB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2021 | TM1401 | 31 | 605 | B | TM140131-SV-605B | TM140131SV605B | Dry End | POPE REEL FRAMEWORK GATE CLOSE | SV | Solenoid Valve | TM140131-SJB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2009 | TM1401 | 31 | 612 | A | TM140131-GE-612A | TM140131GE612A_NO | Dry End | POPE REEL SPOOL LOADER ARMS RISED NO | GE | Limit Switch Element | TM140131-JB-060 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2009 | TM1401 | 31 | 612 | A | TM140131-GE-612A | TM140131GE612A_NC | Dry End | POPE REEL SPOOL LOADER ARMS RISED NC | GE | Limit Switch Element | TM140131-JB-060 | DCS | DI | wet contact, NC | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2009 | TM1401 | 31 | 612 | B | TM140131-GE-612B | TM140131GE612B_NO | Dry End | POPE REEL SPOOL LOADER ARMS LOWERED NO | GE | Limit Switch Element | TM140131-JB-060 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2009 | TM1401 | 31 | 612 | B | TM140131-GE-612B | TM140131GE612B_NC | Dry End | POPE REEL SPOOL LOADER ARMS LOWERED NC | GE | Limit Switch Element | TM140131-JB-060 | DCS | DI | wet contact, NC | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2009 | TM1401 | 31 | 612 | C | TM140131-GE-612C | TM140131GE612C | Dry End | POPE REEL SPOOL LOADER SHAFT IN ARMS FS | GE | Limit Switch Element | TM140131-JB-060 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2016 | TM1401 | 31 | 612 | D | TM140131-GE-612D | TM140131GE612D | Dry End | POPE REEL SPOOL LOADER SHAFT IN ARMS BS | GE | Limit Switch Element | TM140131-JB-560 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2009 | TM1401 | 31 | 612 | E | TM140131-GE-612E | TM140131GE612E | Dry End | POPE REEL SPOOL LOADER SHAFT IN STORAGE FS | GE | Limit Switch Element | TM140131-JB-060 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2016 | TM1401 | 31 | 612 | F | TM140131-GE-612F | TM140131GE612F | Dry End | POPE REEL SPOOL LOADER SHAFT IN STORAGE BS | GE | Limit Switch Element | TM140131-JB-560 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2001 | TM1401 | 31 | 612 | A | TM140131-HS-612A | TM140131HS612A | Dry End | POPE REEL SPOOL LOADER ARMS RISE CMD | HS | Push button | TM140131-CP-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2001 | TM1401 | 31 | 612 | B | TM140131-HS-612B | TM140131HS612B | Dry End | POPE REEL SPOOL LOADER ARMS LOWER CMD | HS | Push button | TM140131-CP-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2005 | TM1401 | 31 | 612 | A | TM140131-XL-612A | TM140131XL612A | Dry End | POPE REEL SPOOL LOADER ARMS RISED IND | XL | Lamp | TM140131-CP-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2005 | TM1401 | 31 | 612 | B | TM140131-XL-612B | TM140131XL612B | Dry End | POPE REEL SPOOL LOADER ARMS LOWERED IND | XL | Lamp | TM140131-CP-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2016 | TM1401 | 31 | 614 |  | TM140131-GE-614 | TM140131GE614 | Dry End | POPE REEL SHEET DETECTION ON BS | GE | Limit Switch Element | TM140131-JB-560 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2001 | TM1401 | 31 | 619 | A | TM140131-HS-619A | TM140131HS619A | Dry End | POPE REEL TURN-UP TRANSFER CMD | HS | Push button | TM140131-CP-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2001 | TM1401 | 31 | 619 | B | TM140131-HS-619B | TM140131HS619B | Dry End | POPE REEL TURN-UP DONE CMD | HS | Push button | TM140131-CP-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2028 | TM1401 | 31 | 619 |  | TM140131-SV-619 | TM140131SV619 | Dry End | POPE REEL TURN-UP SHOWER AIR ON | SV | Solenoid Valve | TM140131-SJB-002 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2015 | TM1401 | 31 | 629 |  | TM140131-GE-629 | TM140131GE629 | Dry End | POPE REEL DEFLECTOR ON THREADING POS. | GE | Limit Switch Element | TM140131-JB-160 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet | [22 empty] | 2
P-OKITM07-329-06-WRD-2021 | TM1401 | 31 | 629 | A | TM140131-SV-629A | TM140131SV629A | Dry End | POPE REEL DEFLECTOR LOAD | SV | Solenoid Valve | TM140131-SJB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2021 | TM1401 | 31 | 629 | B | TM140131-SV-629B | TM140131SV629B | Dry End | POPE REEL DEFLECTOR UNLOAD | SV | Solenoid Valve | TM140131-SJB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2011 | TM1401 | 31 | 642 | A_NO | TM140131-GE-642A_NO | TM140131GE642A_NO | Dry End | POPE REEL PRIMARY ARMS LOWER NO | GE | Limit Switch Element | TM140131-JB-160 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2011 | TM1401 | 31 | 642 | A_NC | TM140131-GE-642A_NC | TM140131GE642A_NC | Dry End | POPE REEL PRIMARY ARMS LOWER NC | GE | Limit Switch Element | TM140131-JB-160 | DCS | DI | wet contact, NC | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2011 | TM1401 | 31 | 642 | B_NO | TM140131-GE-642B_NO | TM140131GE642B_NO | Dry End | POPE REEL PRIMARY ARMS TURN-UP POS. NO | GE | Limit Switch Element | TM140131-JB-160 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2011 | TM1401 | 31 | 642 | B_NC | TM140131-GE-642B_NC | TM140131GE642B_NC | Dry End | POPE REEL PRIMARY ARMS TURN-UP POS. NC | GE | Limit Switch Element | TM140131-JB-160 | DCS | DI | wet contact, NC | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2011 | TM1401 | 31 | 642 | C_NO | TM140131-GE-642C_NO | TM140131GE642C_NO | Dry End | POPE REEL PRIMARY ARMS RAISE NO | GE | Limit Switch Element | TM140131-JB-160 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2011 | TM1401 | 31 | 642 | C_NC | TM140131-GE-642C_NC | TM140131GE642C_NC | Dry End | POPE REEL PRIMARY ARMS RAISE NC | GE | Limit Switch Element | TM140131-JB-160 | DCS | DI | wet contact, NC | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2011 | TM1401 | 31 | 642 | D | TM140131-GE-642D | TM140131GE642D | Dry End | POPE REEL PRIMARY ARMS SHAFT IN ARMS FS | GE | Limit Switch Element | TM140131-JB-160 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2017 | TM1401 | 31 | 642 | E | TM140131-GE-642E | TM140131GE642E | Dry End | POPE REEL PRIMARY ARMS SHAFT IN ARMS BS | GE | Limit Switch Element | TM140131-JB-660 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2002 | TM1401 | 31 | 642 | A | TM140131-HS-642A | TM140131HS642A | Dry End | POPE REEL PRIMARY ARMS LOWERING CMD | HS | Push button | TM140131-CP-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2002 | TM1401 | 31 | 642 | B | TM140131-HS-642B | TM140131HS642B | Dry End | POPE REEL PRIMARY ARMS RAISING CMD | HS | Push button | TM140131-CP-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2005 | TM1401 | 31 | 642 | A | TM140131-XL-642A | TM140131XL642A | Dry End | POPE REEL PRIMARY ARMS LOWERING IND | XL | Lamp | TM140131-CP-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2005 | TM1401 | 31 | 642 | B | TM140131-XL-642B | TM140131XL642B | Dry End | POPE REEL PRIMARY ARMS RAISING IND | XL | Lamp | TM140131-CP-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2010 | TM1401 | 31 | 642 |  | TM140131-GT-642 | TM140131GT642 | Dry End | POPE REEL PRIMARY ARMS POSITION MEASUREMENT | GT | Limit Transmitter | TM140131-JB-060 | DCS | AI | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 0 | 108 | °
P-OKITM07-329-06-WRD-2013 | TM1401 | 31 | 643 | A | TM140131-GE-643A | TM140131GE643A | Dry End | POPE REEL SECONDARY ARMS SPOOL IN ARMS FS | GE | Limit Switch Element | TM140131-JB-260 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2012 | TM1401 | 31 | 643 | C | TM140131-GE-643C | TM140131GE643C | Dry End | POPE REEL SECONDARY ARMS EJECTED FS | GE | Limit Switch Element | TM140131-JB-160 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2002 | TM1401 | 31 | 643 | A | TM140131-HS-643A | TM140131HS643A | Dry End | POPE REEL SECONDARY ARMS LOAD CMD | HS | Push button | TM140131-CP-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2002 | TM1401 | 31 | 643 | B | TM140131-HS-643B | TM140131HS643B | Dry End | POPE REEL SECONDARY ARMS EJECT CMD | HS | Push button | TM140131-CP-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2006 | TM1401 | 31 | 643 | A | TM140131-XL-643A | TM140131XL643A | Dry End | POPE REEL SECONDARY ARMS LOAD IND | XL | Lamp | TM140131-CP-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2006 | TM1401 | 31 | 643 | B | TM140131-XL-643B | TM140131XL643B | Dry End | POPE REEL SECONDARY ARMS EJECT IND | XL | Lamp | TM140131-CP-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2013 | TM1401 | 31 | 643 |  | TM140131-GT-643 | TM140131GT643 | Dry End | POPE REEL SECONDARY ARMS ANGLE MEASUR. | GT | Limit Transmitter | TM140131-JB-260 | DCS | AI | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 0 | 42 | °
P-OKITM07-329-06-WRD-2021 | TM1401 | 31 | 643 | A | TM140131-SV-643A | TM140131SV643A | Dry End | POPE REEL SECONDARY ARMS GAP | SV | Solenoid Valve | TM140131-SJB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2021 | TM1401 | 31 | 643 | B | TM140131-SV-643B | TM140131SV643B | Dry End | POPE REEL SECONDARY ARMS SPOOL LOAD | SV | Solenoid Valve | TM140131-SJB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2021 | TM1401 | 31 | 643 | C | TM140131-SV-643C | TM140131SV643C | Dry End | POPE REEL SECONDARY ARMS SPOOL EJECT | SV | Solenoid Valve | TM140131-SJB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2024 | TM1401 | 31 | 643 | A | TM140131-PT-643A | TM140131PT643A | Dry End | POPE REEL SECONDARY ARMS PRESSURE FS | PT | Pressure Transmitter | TM140131-SJB-001 | DCS | AI | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 0 | 6 | bar
P-OKITM07-329-06-WRD-2024 | TM1401 | 31 | 643 | B | TM140131-PT-643B | TM140131PT643B | Dry End | POPE REEL SECONDARY ARMS PRESSURE BS | PT | Pressure Transmitter | TM140131-SJB-001 | DCS | AI | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 0 | 6 | bar
P-OKITM07-329-06-WRD-2024 | TM1401 | 31 | 643 | C | TM140131-PT-643C | TM140131PT643C | Dry End | POPE REEL SECONDARY ARMS EJECT LINE PRESSURE | PT | Pressure Transmitter | TM140131-SJB-001 | DCS | AI | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 0 | 6 | bar
P-OKITM07-329-06-WRD-2025 | TM1401 | 31 | 643 | A | TM140131-PV-643A | TM140131PV643A | Dry End | POPE REEL SECONDARY ARMS NIP SETPOINT BS | PV | Pressure valve | TM140131-SJB-001 | DCS | AO | 4-20 mA | 24Vdc | 3 | DCS Cabinet | 0 | 5 | bar
P-OKITM07-329-06-WRD-2025 | TM1401 | 31 | 643 | B | TM140131-PV-643B | TM140131PV643B | Dry End | POPE REEL SECONDARY ARMS NIP SETPOINT FS | PV | Pressure valve | TM140131-SJB-001 | DCS | AO | 4-20 mA | 24Vdc | 3 | DCS Cabinet | 0 | 5 | bar
P-OKITM07-329-06-WRD-2002 | TM1401 | 31 | 644 | A | TM140131-HS-644A | TM140131HS644A | Dry End | POPE REEL SPOOL STARTER START CMD | HS | Push button | TM140131-CP-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2002 | TM1401 | 31 | 644 | B | TM140131-HS-644B | TM140131HS644B | Dry End | POPE REEL SPOOL STARTER STOP CMD | HS | Push button | TM140131-CP-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2006 | TM1401 | 31 | 644 | A | TM140131-XL-644A | TM140131XL644A | Dry End | POPE REEL SPOOL STARTER START IND | XL | Lamp | TM140131-CP-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2006 | TM1401 | 31 | 644 | B | TM140131-XL-644B | TM140131XL644B | Dry End | POPE REEL SPOOL STARTER STOP IND | XL | Lamp | TM140131-CP-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2015 | TM1401 | 31 | 648 | C | TM140131-GE-648C | TM140131GE648C | Dry End | POPE REEL WEIGHT STATION SPOOL ON FRAME FS | GE | Limit Switch Element | TM140131-JB-460 | DCS | DI | wet contact, NC | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2019 | TM1401 | 31 | 648 | D | TM140131-GE-648D | TM140131GE648D | Dry End | POPE REEL WEIGHT STATION SPOOL ON FRAME BS | GE | Limit Switch Element | TM140131-JB-860 | DCS | DI | wet contact, NC | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2002 | TM1401 | 31 | 648 | A | TM140131-HS-648A | TM140131HS648A | Dry End | POPE REEL WEIGHT STATION WEIGHT CMD | HS | Push button | TM140131-CP-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2002 | TM1401 | 31 | 648 | B | TM140131-HS-648B | TM140131HS648B | Dry End | POPE REEL WEIGHT STATION LOWER CMD | HS | Push button | TM140131-CP-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2006 | TM1401 | 31 | 648 |  | TM140131-XL-648 | TM140131XL648 | Dry End | POPE REEL WEIGHT STATION WEIGHT IND | XL | Lamp | TM140131-CP-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2015 | TM1401 | 31 | 648 | A | TM140131-WT-648A | TM140131WT648A | Dry End | POPE REEL WEIGHT STATION MEASUREMENT FS | WT | Weight Transmitter | TM140131-JB-460 | DCS | AI | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 0 | 15000 | kg
P-OKITM07-329-06-WRD-2019 | TM1401 | 31 | 648 | B | TM140131-WT-648B | TM140131WT648B | Dry End | POPE REEL WEIGHT STATION MEASUREMENT BS | WT | Weight Transmitter | TM140131-JB-860 | DCS | AI | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 0 | 15000 | kg
P-OKITM07-329-06-WRD-2022 | TM1401 | 31 | 654 | A | TM140131-SV-654A | TM140131SV654A | Dry End | POPE REEL SPOOL STORAGE LOAD | SV | Solenoid Valve | TM140131-SJB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2022 | TM1401 | 31 | 654 | B | TM140131-SV-654B | TM140131SV654B | Dry End | POPE REEL SPOOL STORAGE UNLOAD | SV | Solenoid Valve | TM140131-SJB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2014 | TM1401 | 31 | 677 | A | TM140131-GE-677A | TM140131GE677A | Dry End | POPE REEL SPOOL BRAKE SPOOL ON FRAME FS | GE | Limit Switch Element | TM140131-JB-360 | DCS | DI | wet contact, NC | 24Vdc | 3 | DCS Cabinet | [24 empty] | CHANGED DESCRIPTION
P-OKITM07-329-06-WRD-2018 | TM1401 | 31 | 677 | B | TM140131-GE-677B | TM140131GE677B | Dry End | POPE REEL SPOOL BRAKE SPOOL ON FRAME BS | GE | Limit Switch Element | TM140131-JB-760 | DCS | DI | wet contact, NC | 24Vdc | 3 | DCS Cabinet | [24 empty] | CHANGED DESCRIPTION
P-OKITM07-329-06-WRD-2003 | TM1401 | 31 | 677 | A | TM140131-HS-677A | TM140131HS677A | Dry End | POPE REEL SPOOL BRAKE AUTO CMD | HS | Push button | TM140131-CP-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2003 | TM1401 | 31 | 677 | B | TM140131-HS-677B | TM140131HS677B | Dry End | POPE REEL SPOOL BRAKE RELEASE CMD | HS | Push button | TM140131-CP-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2006 | TM1401 | 31 | 677 | A | TM140131-XL-677A | TM140131XL677A | Dry End | POPE REEL SPOOL BRAKE AUTO IND | XL | Lamp | TM140131-CP-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2006 | TM1401 | 31 | 677 | B | TM140131-XL-677B | TM140131XL677B | Dry End | POPE REEL SPOOL BRAKE RELEASE IND | XL | Lamp | TM140131-CP-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2022 | TM1401 | 31 | 677 | A | TM140131-SV-677A | TM140131SV677A | Dry End | POPE REEL SPOOL BRAKE LOAD | SV | Solenoid Valve | TM140131-SJB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2022 | TM1401 | 31 | 677 | B | TM140131-SV-677B | TM140131SV677B | Dry End | POPE REEL SPOOL BRAKE UNLOAD | SV | Solenoid Valve | TM140131-SJB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2010 | TM1401 | 31 | 690 | A | TM140131-GE-690A | TM140131GE690A | Dry End | POPE REEL PRIMARY ARMS HOOKS CLOSED FS | GE | Limit Switch Element | TM140131-JB-060 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2016 | TM1401 | 31 | 690 | B | TM140131-GE-690B | TM140131GE690B | Dry End | POPE REEL PRIMARY ARMS HOOKS CLOSED BS | GE | Limit Switch Element | TM140131-JB-560 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2010 | TM1401 | 31 | 690 | C | TM140131-GE-690C | TM140131GE690C | Dry End | POPE REEL PRIMARY ARMS HOOKS SPOOL 1ST DIA. | GE | Limit Switch Element | TM140131-JB-060 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2016 | TM1401 | 31 | 690 | D | TM140131-GE-690D | TM140131GE690D | Dry End | POPE REEL PRIMARY ARMS HOOKS SPOOL MAX DIA. | GE | Limit Switch Element | TM140131-JB-560 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2010 | TM1401 | 31 | 690 | E | TM140131-GE-690E | TM140131GE690E | Dry End | POPE REEL PRIMARY ARMS HOOKS OPENED FS | GE | Limit Switch Element | TM140131-JB-060 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2016 | TM1401 | 31 | 690 | F | TM140131-GE-690F | TM140131GE690F | Dry End | POPE REEL PRIMARY ARMS HOOKS OPENED BS | GE | Limit Switch Element | TM140131-JB-560 | DCS | DI | wet contact, NO | 24Vdc | 3 | DCS Cabinet
P-OKITM07-329-06-WRD-2003 | TM1401 | 31 | 690 | A | TM140131-HS-690A | TM140131HS690A | Dry End | POPE REEL PRIMARY ARMS HOOKS CLOSE CMD | HS | Push button | TM140131-CP-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2003 | TM1401 | 31 | 690 | B | TM140131-HS-690B | TM140131HS690B | Dry End | POPE REEL PRIMARY ARMS HOOKS OPEN CMD | HS | Push button | TM140131-CP-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2007 | TM1401 | 31 | 690 | A | TM140131-XL-690A | TM140131XL690A | Dry End | POPE REEL PRIMARY ARMS HOOKS CLOSE IND | XL | Lamp | TM140131-CP-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2007 | TM1401 | 31 | 690 | B | TM140131-XL-690B | TM140131XL690B | Dry End | POPE REEL PRIMARY ARMS HOOKS OPEN IND | XL | Lamp | TM140131-CP-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2020 | TM1401 | 31 | 690 |  | TM140131-PS-690 | TM140131PS690 | Dry End | POPE REEL PRIMARY ARMS HOOKS AIR OK | PS | Pressure Switch | TM140131-SJB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2022 | TM1401 | 31 | 690 | A | TM140131-SV-690A | TM140131SV690A | Dry End | POPE REEL PRIMARY ARMS HOOKS CLOSE | SV | Solenoid Valve | TM140131-SJB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2022 | TM1401 | 31 | 690 | B | TM140131-SV-690B | TM140131SV690B | Dry End | POPE REEL PRIMARY ARMS HOOKS OPEN | SV | Solenoid Valve | TM140131-SJB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2024 | TM1401 | 31 | 690 | A | TM140131-PT-690A | TM140131PT690A | Dry End | POPE REEL PRIMARY ARMS HOOKS PRESSURE ON FS | PT | Pressure Transmitter | TM140131-SJB-001 | DCS | AI | 4-20 mA | 24Vdc | 2 | DCS Cabinet | 0 | 6 | bar
P-OKITM07-329-06-WRD-2024 | TM1401 | 31 | 690 | B | TM140131-PT-690B | TM140131PT690B | Dry End | POPE REEL PRIMARY ARMS HOOKS PRESSURE ON BS | PT | Pressure Transmitter | TM140131-SJB-001 | DCS | AI | 4-20 mA | 24Vdc | 2 | DCS Cabinet | 0 | 6 | bar
P-OKITM07-329-06-WRD-2025 | TM1401 | 31 | 690 | A | TM140131-PV-690A | TM140131PV690A | Dry End | POPE REEL PRIMARY ARMS HOOKS | PV | Pressure valve | TM140131-SJB-001 | DCS | AO | 4-20 mA | 24Vdc | 3 | DCS Cabinet | 0 | 5 | bar
P-OKITM07-329-06-WRD-2025 | TM1401 | 31 | 690 | B | TM140131-PV-690B | TM140131PV690B | Dry End | POPE REEL PRIMARY ARMS HOOKS | PV | Pressure valve | TM140131-SJB-001 | DCS | AO | 4-20 mA | 24Vdc | 3 | DCS Cabinet | 0 | 5 | bar
P-OKITM07-329-06-WRD-2022 | TM1401 | 31 | 695 |  | TM140131-SV-695 | TM140131SV695 | Dry End | POPE REEL PRIMARY ARMS HOOKS LUB ON/OFF | SV | Solenoid Valve | TM140131-SJB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2013 P-OKITM07-329-06-WRD-2003 | TM1401 | 31 | 703 |  | TM140131-HS-703 | TM140131HS703 | Dry End | THREADING SYSTEM AIR ON | HS | Push button | TM140131-CP-001 ¦ TM140131-CB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2015 | TM1401 | 31 | 703 |  | TM140131-XL-703 | TM140131XL703 | Dry End | THREADING SYSTEM AIR ON IND | XL | Lamp | TM140131-CP-001 ¦ TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2028 | TM1401 | 31 | 703 |  | TM140131-SV-703 | TM140131SV703 | Dry End | THREADING SYS TRANSFER TUBES AIR ON | SV | Solenoid Valve | TM140131-SJB-002 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2028 | TM1401 | 31 | 723 |  | TM140131-SV-723 | TM140131SV723 | Dry End | THREADING SYS REEL DRUM BLOWERS ON | SV | Solenoid Valve | TM140131-SJB-002 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2013 P-OKITM07-329-06-WRD-2003 | TM1401 | 31 | 720 |  | TM140131-HS-720 | TM140131HS720 | Dry End | THREADING SYSTEM RUN | HS | Push button | TM140131-CP-001 ¦ TM140131-CB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2028 | TM1401 | 31 | 720 | A | TM140131-SV-720A | TM140131SV720A | Dry End | THREADING SYS TAIL TO UTM | SV | Solenoid Valve | TM140131-SJB-002 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2028 | TM1401 | 31 | 720 | B | TM140131-SV-720B | TM140131SV720B | Dry End | THREADING SYS TAIL TO REEL | SV | Solenoid Valve | TM140131-SJB-002 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2027 | TM1401 | 31 | 764 |  | TM140131-PS-764 | TM140131PS764 | Dry End | THREADING SYS AIR SUPPLY FRAME PRESSURE OK | PS | Pressure Switch | TM140131-SJB-002 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2009 | TM1401 | 31 | 781 | A | TM140131-GE-781A | TM140131GE781A | Dry End | THREADING SYS TAIL CUTTER FRONT POS. | GE | Limit Switch Element | TM140130-JB-303 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2009 | TM1401 | 31 | 781 | B | TM140131-GE-781B | TM140131GE781B | Dry End | THREADING SYS TAIL CUTTER STD POS. | GE | Limit Switch Element | TM140130-JB-303 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2013 P-OKITM07-329-06-WRD-2003 | TM1401 | 31 | 781 | A | TM140131-HS-781A | TM140131HS781A | Dry End | THREADING SYS TAIL CUTTER NARROW CMD | HS | Push button | TM140131-CP-001 ¦ TM140131-CB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2013 P-OKITM07-329-06-WRD-2003 | TM1401 | 31 | 781 | B | TM140131-HS-781B | TM140131HS781B | Dry End | THREADING SYS TAIL CUTTER WIDEN CMD | HS | Push button | TM140131-CP-001 ¦ TM140131-CB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2015 | TM1401 | 31 | 781 | A | TM140131-XL-781A | TM140131XL781A | Dry End | THREADING SYS TAIL CUTTER NARROW IND | XL | Lamp | TM140131-CP-001 ¦ TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2015 | TM1401 | 31 | 781 | B | TM140131-XL-781B | TM140131XL781B | Dry End | THREADING SYS TAIL CUTTER WIDEN IND | XL | Lamp | TM140131-CP-001 ¦ TM140131-CB-001 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-323-06-WRD-2010 | TM1401 | 31 | 781 |  | TM140131-GT-781 | TM140131GT781 | Dry End | THREADING SYS TAIL CUTTER POSITION | GT | Limit Transmitter | TM140130-JB-303 | DCS | AI | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 0 | 3800 | mm
PMP: will be updated in the future | TM1401 | 31 | 781 |  | TM140131-SV-781 | TM140131SV781 | Dry End | THREADING SYS TAIL CUTTER WATER ON | SV | Solenoid Valve | FIELD | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
PMP: will be updated in the future | TM1401 | 31 | 799 |  | TM140131-SV-799 | TM140131SV799 | Dry End | THREADING SYS REEL DRUM VACUUM SHEAVE | SV | Solenoid Valve | FIELD | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet | [24 empty] | REV D
P-OKITM07-333-06-WRD-2002 | TM1401 | 34 | 101 |  | TM140134-TT-101 | TM140134TT101 | Lubrication, Hydraulic system | LUBRICATION UNIT TANK OIL TEMP. | TT | Temp. Transmitter | TM140134-JB-001 | DCS | AI | 4-20 mA | 24Vdc external | 3 | DCS Cabinet | -50 | +150 | ℃
P-OKITM07-333-06-WRD-2002 | TM1401 | 34 | 101 |  | TM140134-LT-101 | TM140134LT101 | Lubrication, Hydraulic system | LUBRICATION UNIT TANK OIL LEVEL MEASUREMENT | LT | Level Transmitter | TM140134-JB-001 | DCS | AI | 4-20 mA | 24Vdc external | 3 | DCS Cabinet
P-OKITM07-333-06-WRD-2003 | TM1401 | 34 | 104 |  | TM140134-PS-104 | TM140134PS104 | Lubrication, Hydraulic system | LUBRICATION UNIT SUPPLY LINE – FILTER OK | PS | Pressure Switch | TM140134-JB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-333-06-WRD-2003 | TM1401 | 34 | 105 |  | TM140134-PV-105 | TM140134PV105 | Lubrication, Hydraulic system | LUBRICATION UNIT COOLING WATER | PV | Pressure valve | TM140134-JB-001 | DCS | AO | 4-20 mA | 24Vdc | 2 | DCS Cabinet | 0 | 100 | %
P-OKITM07-333-06-WRD-2002 | TM1401 | 34 | 106 |  | TM140134-TT-106 | TM140134TT106 | Lubrication, Hydraulic system | LUBRICATION UNIT OIL SUPPLY LINE TEMPERATURE | TT | Temp. Transmitter | TM140134-JB-001 | DCS | AI | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | -50 | +150 | ℃
P-OKITM07-333-06-WRD-2002 | TM1401 | 34 | 106 |  | TM140134-PT-106 | TM140134PT106 | Lubrication, Hydraulic system | LUBRICATION UNIT OIL SUPPLY LINE PRESSURE | PT | Pressure Transmitter | TM140134-JB-001 | DCS | AI | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 0 | 16 | bar
P-OKITM07-333-06-WRD-2005 | TM1401 | 34 | 126 | A | TM140134-FT-126A | TM140134FT126A | Lubrication, Hydraulic system | LUBRICATION UNIT – OIL TO YANKEE BEARING ON FS | FT | Flow Transmitter | TM140134-JB-002 | DCS | AI | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 2 | 11 | L/min
P-OKITM07-333-06-WRD-2005 | TM1401 | 34 | 126 | B | TM140134-FT-126B | TM140134FT126B | Lubrication, Hydraulic system | LUBRICATION UNIT – OIL TO YANKEE BEARING ON BS | FT | Flow Transmitter | TM140134-JB-002 | DCS | AI | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 2 | 11 | L/min
P-OKITM07-333-06-WRD-2005 | TM1401 | 34 | 126 | C | TM140134-FT-126C | TM140134FT126C | Lubrication, Hydraulic system | LUBRICATION UNIT – OIL TO YANKEE GEARBOX | FT | Flow Transmitter | TM140134-JB-002 | DCS | AI | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 1 | 60 | L/min
P-OKITM07-333-06-WRD-2005 | TM1401 | 34 | 127 | A | TM140134-FT-127A | TM140134FT127A | Lubrication, Hydraulic system | LUBRICATION UNIT – OIL TO SPR BEARING ON FS | FT | Flow Transmitter | TM140134-JB-002 | DCS | AI | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 2 | 4.5 | L/min
P-OKITM07-333-06-WRD-2005 | TM1401 | 34 | 127 | B | TM140134-FT-127B | TM140134FT127B | Lubrication, Hydraulic system | LUBRICATION UNIT – OIL TO SPR BEARING ON BS | FT | Flow Transmitter | TM140134-JB-002 | DCS | AI | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 2 | 4.5 | L/min
P-OKITM07-333-06-WRD-2005 | TM1401 | 34 | 142 |  | TM140134-FT-142 | TM140134FT142 | Lubrication, Hydraulic system | LUBRICATION UNIT – OIL TO FORMING ROLL GEARBOX | FT | Flow Transmitter | TM140134-JB-002 | DCS | AI | 4-20 mA | 24Vdc loop | 2 | DCS Cabinet | 2 | 8 | L/min
P-OKITM07-331-06-WRD-2004 | TM1401 | 34 | 801 | A | TM140134-TT-801A | TM140134TT801A | Lubrication, Hydraulic system | HYDRAULIC UNIT TANK OIL TEMP. | TT | Temp. Transmitter | TM140134-HB-001 | DCS | AI | 4-20 mA | 24Vdc | 2 | DCS Cabinet | -25 | +100 | ℃
P-OKITM07-331-06-WRD-2003 | TM1401 | 34 | 801 | A | TM140134-LS-801A | TM140134LS801A | Lubrication, Hydraulic system | HYDRAULIC UNIT TANK OIL LEVEL LOW | LS | Level Switch | TM140134-HB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2003 | TM1401 | 34 | 801 | B | TM140134-LS-801B | TM140134LS801B | Lubrication, Hydraulic system | HYDRAULIC UNIT TANK OIL LEVEL LOW LOW | LS | Level Switch | TM140134-HB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2004 | TM1401 | 34 | 801 |  | TM140134-PS-801 | TM140134PS801 | Lubrication, Hydraulic system | HYDRUALIC UNIT CIRCULATION LINE – FILTER OK | PS | Pressure Switch | TM140134-HB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2003 | TM1401 | 34 | 810 | A | TM140134-PS-810A | TM140134PS810A | Lubrication, Hydraulic system | HYDRUALIC UNIT REEL SUPPLY LINE – FILTER #1 OK | PS | Pressure Switch | TM140134-HB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2003 | TM1401 | 34 | 810 | B | TM140134-PS-810B | TM140134PS810B | Lubrication, Hydraulic system | HYDRUALIC UNIT REEL SUPPLY LINE – FILTER #2 OK | PS | Pressure Switch | TM140134-HB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2004 | TM1401 | 34 | 811 |  | TM140134-PS-811 | TM140134PS811 | Lubrication, Hydraulic system | HYDRUALIC UNIT REEL SUPPLY LINE – OIL PRESSURE OK | PS | Pressure Switch | TM140134-HB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2005 | TM1401 | 34 | 812 |  | TM140134-SV-812 | TM140134SV812 | Lubrication, Hydraulic system | HYDRUALIC UNIT PRESS ROLL SUPPLY LINE – RELIEVING VALVE OPEN | SV | Solenoid Valve | TM140134-HB-001 | DCS | DO | dry contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2003 | TM1401 | 34 | 820 | A | TM140134-PS-820A | TM140134PS820A | Lubrication, Hydraulic system | HYDRUALIC UNIT PRESS ROLL SUPPLY LINE – FILTER #1 OK | PS | Pressure Switch | TM140134-HB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2004 | TM1401 | 34 | 820 | B | TM140134-PS-820B | TM140134PS820B | Lubrication, Hydraulic system | HYDRUALIC UNIT PRESS ROLL SUPPLY LINE – FILTER #2 OK | PS | Pressure Switch | TM140134-HB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2004 | TM1401 | 34 | 821 |  | TM140134-PS-821 | TM140134PS821 | Lubrication, Hydraulic system | HYDRUALIC UNIT PRESS ROLL SUPPLY LINE – OIL PRESSURE OK | PS | Pressure Switch | TM140134-HB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2005 | TM1401 | 34 | 822 |  | TM140134-SV-822 | TM140134SV822 | Lubrication, Hydraulic system | HYDRUALIC UNIT REEL SUPPLY LINE – RELIEVING VALVE OPEN | SV | Solenoid Valve | TM140134-HB-001 | DCS | DO | dry contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2009 | TM1401 | 34 | 648 | A | TM140134-SV-648A | TM140134SV648A | Lubrication, Hydraulic system | HYDRAULIC TABLE WEIGHT STATION – LOWER | SV | Solenoid Valve | TM140134-HB-002 | DCS | DO | dry contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2009 | TM1401 | 34 | 648 | B | TM140134-SV-648B | TM140134SV648B | Lubrication, Hydraulic system | HYDRAULIC TABLE WEIGHT STATION – LIFT | SV | Solenoid Valve | TM140134-HB-002 | DCS | DO | dry contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2009 | TM1401 | 34 | 612 | A | TM140134-SV-612A | TM140134SV612A | Lubrication, Hydraulic system | HYDRAULIC TABLE SPOOL LOADER – LOWER | SV | Solenoid Valve | TM140134-HB-002 | DCS | DO | dry contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2009 | TM1401 | 34 | 612 | B | TM140134-SV-612B | TM140134SV612B | Lubrication, Hydraulic system | HYDRAULIC TABLE SPOOL LOADER – LIFT | SV | Solenoid Valve | TM140134-HB-002 | DCS | DO | dry contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2008 | TM1401 | 34 | 642 | A | TM140134-SV-642A | TM140134SV642A | Lubrication, Hydraulic system | HYDRAULIC TABLE PRIMARY ARMS – LOWER | SV | Solenoid Valve | TM140134-HB-002 | DCS | DO | dry contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2008 | TM1401 | 34 | 642 | B | TM140134-SV-642B | TM140134SV642B | Lubrication, Hydraulic system | HYDRAULIC TABLE PRIMARY ARMS – LIFT | SV | Solenoid Valve | TM140134-HB-002 | DCS | DO | dry contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2012 | TM1401 | 34 | 691 | _SP | TM140134-PV-691_SP | TM140134PV691_SP | Lubrication, Hydraulic system | HYDRAULIC TABLE PRIMARY ARMS NIP RELIEVING – PRESSURE SETTING | PV | Pressure valve | TM140134-HB-002 | DCS | AO | 4-20 mA | 24Vdc | 2 | DCS Cabinet | 0 | 230 | bar
P-OKITM07-331-06-WRD-2015 | TM1401 | 34 | 691 | A | TM140134-PT-691A | TM140134PT691A | Lubrication, Hydraulic system | HYDRAULIC TABLE PRIMARY ARMS NIP RELIEVING – PRESSURE MESURMENT | PT | Pressure Transmitter | TM140134-HB-002 | DCS | AI | 4-20 mA | 24Vdc | 2 | DCS Cabinet | 0 | 100 | bar
P-OKITM07-331-06-WRD-2015 | TM1401 | 34 | 691 | B | TM140134-PT-691B | TM140134PT691B | Lubrication, Hydraulic system | HYDRAULIC TABLE PRIMARY ARMS NIP RELIEVING – BACK PRESSURE MESURMENT | PT | Pressure Transmitter | TM140134-HB-002 | DCS | AI | 4-20 mA | 24Vdc | 2 | DCS Cabinet | 0 | 100 | bar
P-OKITM07-331-06-WRD-2007 | TM1401 | 34 | 691 | _RY | TM140134-PV-691_RY | TM140134PV691_RY | Lubrication, Hydraulic system | HYDRAULIC TABLE PRIMARY ARMS NIP RELIEVING – READY IND | PV | Pressure valve | TM140134-HB-002 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2007 | TM1401 | 34 | 691 | _STR | TM140134-PV-691_STR | TM140134PV691_STR | Lubrication, Hydraulic system | HYDRAULIC TABLE PRIMARY ARMS NIP RELIEVING ON CMD | PV | Pressure valve | TM140134-HB-002 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2008 | TM1401 | 34 | 316 | A | TM140134-SV-316A | TM140134SV316A | Lubrication, Hydraulic system | HYDRAULIC TABLE PRESS LOADING CLOSE | SV | Solenoid Valve | TM140134-HB-002 | DCS | DO | dry contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2008 | TM1401 | 34 | 316 | B | TM140134-SV-316B | TM140134SV316B | Lubrication, Hydraulic system | HYDRAULIC TABLE PRESS LOADING OPEN | SV | Solenoid Valve | TM140134-HB-002 | DCS | DO | dry contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2010 | TM1401 | 34 | 316 | A_SP | TM140134-PV-316A_SP | TM140134PV316A_SP | Lubrication, Hydraulic system | HYDRAULIC TABLE PRESS LOADING NIP TS PRESSURE SETTING | PV | Pressure valve | TM140134-HB-002 | DCS | AO | 4-20 mA | 24Vdc | 2 | DCS Cabinet | 0 | 230 | bar
P-OKITM07-331-06-WRD-2011 | TM1401 | 34 | 316 | B_SP | TM140134-PV-316B_SP | TM140134PV316B_SP | Lubrication, Hydraulic system | HYDRAULIC TABLE PRESS LOADING NIP DS PRESSURE SETTING | PV | Pressure valve | TM140134-HB-002 | DCS | AO | 4-20 mA | 24Vdc | 2 | DCS Cabinet | 0 | 230 | bar
P-OKITM07-331-06-WRD-2015 | TM1401 | 34 | 316 | A | TM140134-PT-316A | TM140134PT316A | Lubrication, Hydraulic system | HYDRAULIC TABLE PRESS LOADING NIP TS PRESSURE MEASURE | PT | Pressure Transmitter | TM140134-HB-002 | DCS | AI | 4-20 mA | 24Vdc | 2 | DCS Cabinet | 0 | 100 | bar
P-OKITM07-331-06-WRD-2015 | TM1401 | 34 | 316 | B | TM140134-PT-316B | TM140134PT316B | Lubrication, Hydraulic system | HYDRAULIC TABLE PRESS LOADING NIP DS PRESSURE MEASURE | PT | Pressure Transmitter | TM140134-HB-002 | DCS | AI | 4-20 mA | 24Vdc | 2 | DCS Cabinet | 0 | 100 | bar
P-OKITM07-331-06-WRD-2015 | TM1401 | 34 | 316 | C | TM140134-PT-316C | TM140134PT316C | Lubrication, Hydraulic system | HYDRAULIC TABLE PRESS LOADING NIP BACK PRESSURE MEASURE | PT | Pressure Transmitter | TM140134-HB-002 | DCS | AI | 4-20 mA | 24Vdc | 2 | DCS Cabinet | 0 | 100 | bar
P-OKITM07-331-06-WRD-2007 | TM1401 | 34 | 316 | A_RY | TM140134-PV-316A_RY | TM140134PV316A_RY | Lubrication, Hydraulic system | HYDRAULIC TABLE PRESS LOADING TS READY IND | PV | Pressure valve | TM140134-HB-002 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2007 | TM1401 | 34 | 316 | B_RY | TM140134-PV-316B_RY | TM140134PV316B_RY | Lubrication, Hydraulic system | HYDRAULIC TABLE PRESS LOADING DS READY IND | PV | Pressure valve | TM140134-HB-002 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2008 | TM1401 | 34 | 316 | A_STR | TM140134-PV-316A_STR | TM140134PV316A_STR | Lubrication, Hydraulic system | HYDRAULIC TABLE PRESS LOADING TS ON CMD | PV | Pressure valve | TM140134-HB-002 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-331-06-WRD-2008 | TM1401 | 34 | 316 | B_STR | TM140134-PV-316B_STR | TM140134PV316B_STR | Lubrication, Hydraulic system | HYDRAULIC TABLE PRESS LOADING DS ON CMD | PV | Pressure valve | TM140134-HB-002 | DCS | DO | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2046 | TM1401 | 34 | 648 | A | TM140134-ESV-648A | TM140134ESV648A | Lubrication, Hydraulic system | REEL SAFETY - WEIGHT STATION ARMS BLOCKED - SAFETY VALVE #1 | ESV | Safety Solenoid Valve | TM140134-HB-002 | SAFETY PLC | DO | wet contact, NO | 24Vdc | 2 | SAFETY PLC
P-OKITM07-329-06-WRD-2046 | TM1401 | 34 | 648 | B | TM140134-ESV-648B | TM140134ESV648B | Lubrication, Hydraulic system | REEL SAFETY - WEIGHT STATION ARMS BLOCKED - SAFETY VALVE #2 | ESV | Safety Solenoid Valve | TM140134-HB-002 | SAFETY PLC | DO | wet contact, NO | 24Vdc | 2 | SAFETY PLC
P-OKITM07-329-06-WRD-2046 | TM1401 | 34 | 648 | A | TM140134-GSE-648A | TM140134GSE648A | Lubrication, Hydraulic system | REEL SAFETY - WEIGHT STATION ARMS STOPED - SAFETY LIMIT SWITCH #1 | GSE | Safety Limit Switch Element | TM140134-HB-002 | SAFETY PLC | DI | wet contact, NO | 24Vdc | 2 | SAFETY PLC
P-OKITM07-329-06-WRD-2046 | TM1401 | 34 | 648 | B | TM140134-GSE-648B | TM140134GSE648B | Lubrication, Hydraulic system | REEL SAFETY - WEIGHT STATION ARMS STOPED - SAFETY LIMIT SWITCH #2 | GSE | Safety Limit Switch Element | TM140134-HB-002 | SAFETY PLC | DI | wet contact, NO | 24Vdc | 2 | SAFETY PLC
P-OKITM07-332-06-WRD-2010 | TM1401 | 34 | 210 | _STR | TM140134-M-210_STR | TM140134M210_STR | Lubrication, Hydraulic system | GREASE UNIT ON/OFF | M | Start/Stop signal | TM140134-CB-001 | DCS | DO | dry contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-332-06-WRD-2010 | TM1401 | 34 | 210 | _RY | TM140134-M-210_RY | TM140134M210_RY | Lubrication, Hydraulic system | GREASE UNIT FAULT | M | Ready signal | TM140134-CB-001 | DCS | DI | wet contact, NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 003 |  | TM140132TT003 | TM140132TT003 | Burner & Hood System | TEMPERATURE TRANSMITTER - SHC Outlet - WE Hood Inlet | TT | Temp. Transmitter | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 220 | °C
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 007 |  | TM140132TT007 | TM140132TT007 | Burner & Hood System | TEMPERATURE TRANSMITTER - SHC Outlet - DE Hood Inlet | TT | Temp. Transmitter | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 220 | °C
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 008 |  | TM140132TT008 | TM140132TT008 | Burner & Hood System | TEMPERATURE TRANSMITTER - DE Hood Outlet | TT | Temp. Transmitter | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 220 | °C
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 004 |  | TM140132TT004 | TM140132TT004 | Burner & Hood System | TEMPERATURE TRANSMITTER - WE Recirculating FAN Inlet | TT | Temp. Transmitter | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 220 | °C
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 010 |  | TM140132TT010 | TM140132TT010 | Burner & Hood System | TEMPERATURE TRANSMITTER - DE Recirculating FAN Inlet | TT | Temp. Transmitter | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 220 | °C
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 013 |  | TM140132TT013 | TM140132TT013 | Burner & Hood System | TEMPERATURE TRANSMITTER - Fresch Air | TT | Temp. Transmitter | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 220 | °C
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 016 |  | TM140132TT016 | TM140132TT016 | Burner & Hood System | TEMPERATURE TRANSMITTER - Make Up | TT | Temp. Transmitter | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 220 | °C
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 017 |  | TM140132TT017 | TM140132TT017 | Burner & Hood System | TEMPERATURE TRANSMITTER - ON BOARD MOIST.TRANSMITTER - EXHAUST TEMP | TT | Temp. Transmitter | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 220 | °C
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 017 |  | TM140132MT017 | TM140132MT017 | Burner & Hood System | HUMIDITY / TEMPERATURE Sensor for Yankee Exhaust Air Control | MT | Moisture Transmitter | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | -1500 | +1500 | Pa
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 015 |  | TM140132PT015 | TM140132PT015 | Burner & Hood System | Pressure Transmitter for Make-up FAN Control | PT | Pressure Transmitter | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 300 | g/kg
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 005 | AB | TM140132PS005 | TM140132PS005AB | Burner & Hood System | FILTER PRESSURE Switch | PS | PRESSURE SWITCH | FIELD | DCS | DI | NO | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 005 | CD | TM140132PS005 | TM140132PS005CD | Burner & Hood System | FILTER PRESSURE Switch | PS | PRESSURE SWITCH | FIELD | DCS | DI | NO | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 6 | AB | TM140132PS6 | TM140132PS6AB | Burner & Hood System | FILTER PRESSURE Switch | PS | PRESSURE SWITCH | FIELD | DCS | DI | NO | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 006 | CD | TM140132PS006 | TM140132PS006CD | Burner & Hood System | FILTER PRESSURE Switch | PS | PRESSURE SWITCH | FIELD | DCS | DI | NO | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 012 |  | TM140132PS012 | TM140132PS012 | Burner & Hood System | PRESSURE LIMIT SWITCH - PDSAH (HER01 Fresh air filter) | PS | PRESSURE SWITCH | FIELD | DCS | DI | NO | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 018 |  | TM140132PS018 | TM140132PS018 | Burner & Hood System | PRESSURE LIMIT SWITCH - PDSAL 310-311 (Exhaust Interlocks) | PS | PRESSURE SWITCH | FIELD | DCS | DI | NO | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 019 |  | TM140132PS019 | TM140132PS019 | Burner & Hood System | PRESSURE LIMIT SWITCH - PDSAL 310-311 (Exhaust Interlocks) | PS | PRESSURE SWITCH | FIELD | DCS | DI | NO | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 006A |  | TM140132ZSC006A | TM140132ZSC006A | Burner & Hood System | Inductive sensor (WE Hood open) | ZSC | Close limit switch signal | TM140130-JB-103 | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 006A |  | TM140132ZSO006A | TM140132ZSO006A | Burner & Hood System | Inductive sensor (WE Hood close) | ZSO | Open limit switch signal | TM140130-JB-103 | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 006B |  | TM140132ZSC006B | TM140132ZSC006B | Burner & Hood System | Inductive sensor (WE Hood open) | ZSC | Close limit switch signal | TM140130-JB-103 | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 006B |  | TM140132ZSO006B | TM140132ZSO006B | Burner & Hood System | Inductive sensor (WE Hood close) | ZSO | Open limit switch signal | TM140130-JB-103 | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 011A |  | TM140132ZSC011A | TM140132ZSC011A | Burner & Hood System | Inductive sensor (DE Hood open) | ZSC | Close limit switch signal | TM140130-JB-103 | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 011A |  | TM140132ZSO011A | TM140132ZSO011A | Burner & Hood System | Inductive sensor (DE Hood close) | ZSO | Open limit switch signal | TM140130-JB-103 | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 011B |  | TM140132ZSC011B | TM140132ZSC011B | Burner & Hood System | Inductive sensor (DE Hood open) | ZSC | Close limit switch signal | TM140130-JB-103 | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2001 | TM1401 | 32 | 011B |  | TM140132ZSO011B | TM140132ZSO011B | Burner & Hood System | Inductive sensor (DE Hood close) | ZSO | Open limit switch signal | TM140130-JB-103 | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-329-06-WRD-2004 | TM1401 | 32 | 006 | O | TM140132HS006O | TM140132HS006O | Burner & Hood System | HOOD CONTROL WET END OPEN CMD | HS | Push button | TM140131-CP-001 | DCS | DI | NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2004 | TM1401 | 32 | 006 | C | TM140132HS006C | TM140132HS006C | Burner & Hood System | HOOD CONTROL WET END CLOSE CMD | HS | Push button | TM140131-CP-001 | DCS | DI | NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2004 | TM1401 | 32 | 011 | O | TM140132HS011O | TM140132HS011O | Burner & Hood System | HOOD CONTROL DRY END OPEN CMD | HS | Push button | TM140131-CP-001 | DCS | DI | NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2004 | TM1401 | 32 | 011 | C | TM140132HS011C | TM140132HS011C | Burner & Hood System | HOOD CONTROL DRY END CLOSE CMD | HS | Push button | TM140131-CP-001 | DCS | DI | NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2007 | TM1401 | 32 | 006 | O | TM140132XL006O | TM140132XL006O | Burner & Hood System | HOOD CONTROL WET END OPEN IND | XL | Lamp | TM140131-CP-001 | DCS | DO | NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2007 | TM1401 | 32 | 006 | C | TM140132XL006C | TM140132XL006C | Burner & Hood System | HOOD CONTROL WET END CLOSE IND | XL | Lamp | TM140131-CP-001 | DCS | DO | NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2008 | TM1401 | 32 | 011 | O | TM140132XL011O | TM140132XL011O | Burner & Hood System | HOOD CONTROL DRY END OPEN IND | XL | Lamp | TM140131-CP-001 | DCS | DO | NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-329-06-WRD-2008 | TM1401 | 32 | 011 | C | TM140132XL011C | TM140132XL011C | Burner & Hood System | HOOD CONTROL DRY END CLOSE IND | XL | Lamp | TM140131-CP-001 | DCS | DO | NO | 24Vdc | 2 | DCS Cabinet
P-OKITM07-325-08-PID-2002 | TM1401 | 32 | 005 | AC | TM140132ZS005AC | TM140132ZS005AC | Burner & Hood System | Limit Switch (WE-FILTER In / Out) | ZS | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2002 | TM1401 | 32 | 005 | AO | TM140132ZS005AO | TM140132ZS005AO | Burner & Hood System | Limit Switch (WE-FILTER In / Out) | ZS | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2002 | TM1401 | 32 | 005 | BC | TM140132ZS005BC | TM140132ZS005BC | Burner & Hood System | Limit Switch (WE-FILTER In / Out) | ZS | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2002 | TM1401 | 32 | 005 | BO | TM140132ZS005BO | TM140132ZS005BO | Burner & Hood System | Limit Switch (WE-FILTER In / Out) | ZS | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2002 | TM1401 | 32 | 005 | CC | TM140132ZS005CC | TM140132ZS005CC | Burner & Hood System | Limit Switch (WE-FILTER In / Out) | ZS | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2002 | TM1401 | 32 | 005 | CO | TM140132ZS005CO | TM140132ZS005CO | Burner & Hood System | Limit Switch (WE-FILTER In / Out) | ZS | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2002 | TM1401 | 32 | 005 | DC | TM140132ZS005DC | TM140132ZS005DC | Burner & Hood System | Limit Switch (WE-FILTER In / Out) | ZS | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2002 | TM1401 | 32 | 005 | DO | TM140132ZS005DO | TM140132ZS005DO | Burner & Hood System | Limit Switch (WE-FILTER In / Out) | ZS | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2002 | TM1401 | 32 | 006 | AC | TM140132ZS006AC | TM140132ZS006AC | Burner & Hood System | Limit Switch (DE-FILTER In / Out) | ZS | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2002 | TM1401 | 32 | 006 | AO | TM140132ZS006AO | TM140132ZS006AO | Burner & Hood System | Limit Switch (DE-FILTER In / Out) | ZS | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2002 | TM1401 | 32 | 006 | BC | TM140132ZS006BC | TM140132ZS006BC | Burner & Hood System | Limit Switch (DE-FILTER In / Out) | ZS | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2002 | TM1401 | 32 | 006 | BO | TM140132ZS006BO | TM140132ZS006BO | Burner & Hood System | Limit Switch (DE-FILTER In / Out) | ZS | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2002 | TM1401 | 32 | 006 | CC | TM140132ZS006CC | TM140132ZS006CC | Burner & Hood System | Limit Switch (DE-FILTER In / Out) | ZS | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2002 | TM1401 | 32 | 006 | CO | TM140132ZS006CO | TM140132ZS006CO | Burner & Hood System | Limit Switch (DE-FILTER In / Out) | ZS | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2002 | TM1401 | 32 | 006 | DC | TM140132ZS006DC | TM140132ZS006DC | Burner & Hood System | Limit Switch (DE-FILTER In / Out) | ZS | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-325-08-PID-2002 | TM1401 | 32 | 006 | DO | TM140132ZS006DO | TM140132ZS006DO | Burner & Hood System | Limit Switch (DE-FILTER In / Out) | ZS | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 015 |  | TM140135TT015 | TM140135TT015 | Steam & Condensate | TEMPERATURE TRASMITTER-High Press. Steam Feeding | TT | Temp. Transmitter | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 250 | °C
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 016 |  | TM140135PT016 | TM140135PT016 | Steam & Condensate | PRESSURE TRANSMITTER-High Press. Steam Feeding | PT | Pressure Transmitter | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 25 | bar(g)
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 017 |  | TM140135FT017 | TM140135FT017 | Steam & Condensate | STEAM FLOW TRANSMITTER-High Press. Steam Feeding | FT | Flow Transmitter | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 7.500 | kg/h
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 001 |  | TM140135TT001 | TM140135TT001 | Steam & Condensate | TEMPERATURE TRASMITTER-Low Press. Steam Feeding | TT | Temp. Transmitter | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 250 | °C
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 002 |  | TM140135PT002 | TM140135PT002 | Steam & Condensate | PRESSURE TRANSMITTER-Low Press. Steam Feeding | PT | Pressure Transmitter | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 15 | bar(g)
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 003 |  | TM140135FT003 | TM140135FT003 | Steam & Condensate | Flow transmitter-Low Press. Steam Feeding | FT | Flow Transmitter | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 10.500 | kg/h
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 004A |  | TM140135PV004A | TM140135PV004A | Steam & Condensate | STEAM EJECTOR – THERMO-COMPRESSOR TYPE | PV | Pressure valve | FIELD | DCS | AO | 4-20mA N.C. | 24Vdc |  | DCS Cabinet | 0 | 100 | %
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 004B |  | TM140135PV004B | TM140135PV004B | Steam & Condensate | REGULATION VALVE - Make up | PV | Pressure valve | FIELD | DCS | AO | 4-20mA N.C. | 24Vdc |  | DCS Cabinet | 0 | 100 | %
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 004 |  | TM140135PT004 | TM140135PT004 | Steam & Condensate | PRESSURE TRANSMITTER | PT | Pressure Transmitter | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 12 | bar(g)
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 005 |  | TM140135TV005 | TM140135TV005 | Steam & Condensate | REGULATION VALVE - Warm up | TV | TEMPERATURE VALVE | FIELD | DCS | AO | 4-20mA N.C. | 24Vdc |  | DCS Cabinet | 0 | 100 | %
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 005 |  | TM140135TT005 | TM140135TT005 | Steam & Condensate | TEMPERATURE TRASMITTER-Warm up | TT | Temp. Transmitter | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 220 | °C
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 006 |  | TM140135PDT006 | TM140135PDT006 | Steam & Condensate | DIFFERENTIAL PRESSURE TRANSMITTER | PDT | DIFFERENTIAL PRESSURE TRANSMITTER | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 2,0 | bar(g)
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 007 |  | TM140135FT007 | TM140135FT007 | Steam & Condensate | Flow transmitter-blowtrought | FT | Flow Transmitter | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 2.100 | mc/h
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 007A |  | TM140135FV007A | TM140135FV007A | Steam & Condensate | REGULATION VALVE -suct. Thermocomp. | FV | FLOW CONTROL VALVE | FIELD | DCS | AO | 4-20mA N.C. | 24Vdc |  | DCS Cabinet | 0 | 100 | %
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 007B |  | TM140135FV007B | TM140135FV007B | Steam & Condensate | REGULATION VALVE-VENT | FV | FLOW CONTROL VALVE | FIELD | DCS | AO | 4-20mA N.O. | 24Vdc |  | DCS Cabinet | 0 | 100 | %
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 008 |  | TM140135LT008 | TM140135LT008 | Steam & Condensate | LEVEL TRASMITTER | LT | LEVEL TRASMITTER | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 100 | %
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 009 |  | TM140135HLS009 | TM140135HLS009 | Steam & Condensate | HIGH LEVEL SWITCH | HLS | LEVEL TRASMITTER | FIELD | DCS | DI | N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 009 |  | TM140135LLS009 | TM140135LLS009 | Steam & Condensate | LOW LEVEL SWITCH | LLS | LEVEL SWITCH | FIELD | DCS | DI | N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 008 |  | TM140135LV008 | TM140135LV008 | Steam & Condensate | LEVEL CONTROL VALVE YANKEE CONDENSATE | LV | LEVEL VALVE | FIELD | DCS | AO | 4-20mA N.O. | 24Vdc |  | DCS Cabinet | 8 | 100 | %
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 009 |  | TM140135SV009 | TM140135SV009 | Steam & Condensate | SOLENOID | SV | Solenoid Valve | FIELD | DCS | DO | 24 VDC N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 010 |  | TM140135TV010 | TM140135TV010 | Steam & Condensate | TEMPERATURE CONTROL VALVE MAKE UP AIR | TV | TEMPERATURE VALVE | FIELD | DCS | AO | 4-20mA N.O. STRAIGHT WAY | 24Vdc |  | DCS Cabinet | 0 | 100 | %
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 011 |  | TM140135TV011 | TM140135TV011 | Steam & Condensate | TEMPERATURE CONTROL VALVE WE HOOD | TV | TEMPERATURE VALVE | FIELD | DCS | AO | 4-20mA N.C. | 24Vdc |  | DCS Cabinet | 0 | 100 | %
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 012 |  | TM140135TV012 | TM140135TV012 | Steam & Condensate | TEMPERATURE CONTROL VALVE WE HOOD | TV | TEMPERATURE VALVE | FIELD | DCS | AO | 4-20mA N.C. | 24Vdc |  | DCS Cabinet | 0 | 100 | %
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 013 |  | TM140135LT013 | TM140135LT013 | Steam & Condensate | LEVEL TRASMITTER | LT | LEVEL TRASMITTER | FIELD | DCS | AI | 4-20mA | 24Vdc |  | DCS Cabinet | 0 | 100 | %
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 014 |  | TM140135HLS014 | TM140135HLS014 | Steam & Condensate | HIGH LIMIT SWITCH | HLS | LEVEL SWITCH | FIELD | DCS | DI | N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 014 |  | TM140135LLS014 | TM140135LLS014 | Steam & Condensate | LOW LEVEL SWITCH | LLS | LEVEL SWITCH | FIELD | DCS | DI | N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 013 |  | TM140135LV013 | TM140135LV013 | Steam & Condensate | LEVEL CONTROL VALVE HOOD CONDENSATE | LV | LEVEL VALVE | FIELD | DCS | AO | 4-20mA N.O. | 24Vdc |  | DCS Cabinet | 8 | 100 | %
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 014 |  | TM140135SV014 | TM140135SV014 | Steam & Condensate | SOLENOID | SV | Solenoid Valve | FIELD | DCS | DO | 24 VDC N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 020 |  | TM140135TV020 | TM140135TV020 | Steam & Condensate | REGULATION VALVE - Flume | TV | TEMPERATURE VALVE | FIELD | DCS | AO | 4-20mA N.C. | 24Vdc |  | DCS Cabinet | 0 | 100 | %
P-OKITM07-324-08-PID-2001 | TM1401 | 35 | 020 |  | TM140135TT020 | TM140135TT020 | Steam & Condensate | TEMPERATURE TRASMITTER - Flume | TT | Temp. Transmitter | FIELD | DCS | AI | 4-20 mA | 24Vdc |  | DCS Cabinet | 0 | 250 | °C
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 004 |  | TM140133MT004 | TM140133MT004 | Dust Removal & Mist Removal | HUMIDITY AND TEMPERATURE TRASMITTER | MT | Moisture Transmitter | FIELD | DCS | AI | 4-20 mA | 24Vdc |  | DCS Cabinet | 0 | 300 | g/kg
P-OKITM07-335-08-PID-2002 | TM1401 | 33 | 004 |  | TM140133TT004 | TM140133TT004 | Dust Removal & Mist Removal | TEMPERATURE TRASMITTER-Suction Box | TT | Temp. Transmitter | FIELD | DCS | AI | 4-20 mA | 24Vdc |  | DCS Cabinet | 0 | 100 | °C
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 004 |  | TM140133FV004 | TM140133FV004 | Dust Removal & Mist Removal | REGULATION VALVE SPRAY WATER | FV | CONTROL VALVE | FIELD | DCS | AO | 4-20mA N.C. | 24Vdc |  | DCS Cabinet | 0 | 100 | %
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 005 |  | TM140133MT005 | TM140133MT005 | Dust Removal & Mist Removal | HUMIDITY AND TEMPERATURE TRASMITTER | MT | Moisture Transmitter | FIELD | DCS | AI | 4-20 mA | 24Vdc |  | DCS Cabinet | 0 | 300 | g/kg
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 005 |  | TM140133TT005 | TM140133TT005 | Dust Removal & Mist Removal | TEMPERATURE TRASMITTER-Suction Box | TT | Temp. Transmitter | FIELD | DCS | AI | 4-20 mA | 24Vdc |  | DCS Cabinet | 0 | 100 | °C
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 005 |  | TM140133FV005 | TM140133FV005 | Dust Removal & Mist Removal | REGULATION VALVE SPRAY WATER | FV | CONTROL VALVE | FIELD | DCS | AO | 4-20mA N.C. | 24Vdc |  | DCS Cabinet | 0 | 100 | %
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 006 |  | TM140133MT006 | TM140133MT006 | Dust Removal & Mist Removal | HUMIDITY AND TEMPERATURE TRASMITTER | MT | Moisture Transmitter | FIELD | DCS | AI | 4-20 mA | 24Vdc |  | DCS Cabinet | 0 | 300 | g/kg
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 006 |  | TM140133TT006 | TM140133TT006 | Dust Removal & Mist Removal | TEMPERATURE TRASMITTER-Suction Box | TT | Temp. Transmitter | FIELD | DCS | AI | 4-20 mA | 24Vdc |  | DCS Cabinet | 0 | 100 | °C
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 006 |  | TM140133FV006 | TM140133FV006 | Dust Removal & Mist Removal | REGULATION VALVE SPRAY WATER | FV | CONTROL VALVE | FIELD | DCS | AO | 4-20mA N.C. | 24Vdc |  | DCS Cabinet | 0 | 100 | %
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 007 |  | TM140133MT007 | TM140133MT007 | Dust Removal & Mist Removal | HUMIDITY AND TEMPERATURE TRASMITTER | MT | Moisture Transmitter | FIELD | DCS | AI | 4-20 mA | 24Vdc |  | DCS Cabinet | 0 | 300 | g/kg
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 007 |  | TM140133TT007 | TM140133TT007 | Dust Removal & Mist Removal | TEMPERATURE TRASMITTER-Suction Box | TT | Temp. Transmitter | FIELD | DCS | AI | 4-20 mA | 24Vdc |  | DCS Cabinet | 0 | 100 | °C
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 007 |  | TM140133FV007 | TM140133FV007 | Dust Removal & Mist Removal | REGULATION VALVE SPRAY WATER | FV | CONTROL VALVE | FIELD | DCS | AO | 4-20mA N.C. | 24Vdc |  | DCS Cabinet | 0 | 100 | %
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 008 |  | TM140133MT008 | TM140133MT008 | Dust Removal & Mist Removal | HUMIDITY AND TEMPERATURE TRASMITTER | MT | Moisture Transmitter | FIELD | DCS | AI | 4-20 mA | 24Vdc |  | DCS Cabinet | 0 | 300 | g/kg
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 008 |  | TM140133TT008 | TM140133TT008 | Dust Removal & Mist Removal | TEMPERATURE TRASMITTER-Suction Box | TT | Temp. Transmitter | FIELD | DCS | AI | 4-20 mA | 24Vdc |  | DCS Cabinet | 0 | 100 | °C
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 008 |  | TM140133FV008 | TM140133FV008 | Dust Removal & Mist Removal | REGULATION VALVE SPRAY WATER | FV | CONTROL VALVE | FIELD | DCS | AO | 4-20mA N.C. | 24Vdc |  | DCS Cabinet | 0 | 100 | %
P-OKITM07-335-08-PID-2002 | TM1401 | 33 | 40 |  | TM140133MT40 | TM140133MT40 | Dust Removal & Mist Removal | HUMIDITY AND TEMPERATURE TRASMITTER | MT | Moisture Transmitter | FIELD | DCS | AI | 4-20 mA | 24Vdc |  | DCS Cabinet | 0 | 300 | g/kg
P-OKITM07-335-08-PID-2002 | TM1401 | 33 | 40 |  | TM140133TT40 | TM140133TT40 | Dust Removal & Mist Removal | TEMPERATURE TRASMITTER-Suction Box | TT | Temp. Transmitter | FIELD | DCS | AI | 4-20 mA | 24Vdc |  | DCS Cabinet | 0 | 100 | °C
P-OKITM07-335-08-PID-2002 | TM1401 | 33 | 40 |  | TM140133FV40 | TM140133FV40 | Dust Removal & Mist Removal | REGULATION VALVE SPRAY WATER | FV | CONTROL VALVE | FIELD | DCS | AO | 4-20mA N.C. | 24Vdc |  | DCS Cabinet | 0 | 100 | %
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 009 |  | TM140133SV009 | TM140133SV009 | Dust Removal & Mist Removal | SOLENOID VALVE UP-DOWN | SV | Solenoid Valve | FIELD | DCS | DO | 24VDC N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 009 |  | TM140133ZSC009 | TM140133ZSC009 | Dust Removal & Mist Removal | INDUCTIVE SENSOR | ZSC | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 009 |  | TM140133ZSO009 | TM140133ZSO009 | Dust Removal & Mist Removal | INDUCTIVE SENSOR | ZSO | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 030 |  | TM140133SV030 | TM140133SV030 | Dust Removal & Mist Removal | SOLENOID VALVE UP-DOWN | SV | Solenoid Valve | FIELD | DCS | DO | 24VDC N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 030 |  | TM140133ZSC030 | TM140133ZSC030 | Dust Removal & Mist Removal | INDUCTIVE SENSOR | ZSC | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 030 |  | TM140133ZSO030 | TM140133ZSO030 | Dust Removal & Mist Removal | INDUCTIVE SENSOR | ZSO | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 030 |  | TM140133XS030 | TM140133XS030 | Dust Removal & Mist Removal | PAPER BREAK PHOTOCELL | XS | PHOTO CELL SWITCH | FIELD | DCS | DI | N.O | 24Vdc |  | DCS Cabinet
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 003 |  | TM140133LT003 | TM140133LT003 | Dust Removal & Mist Removal | DIFFERENTIAL PRESSURE TRANSMITTER AS LEVEL TRANSMITTER | LT | DIFF. PRESSURE TRANSMITTER | FIELD | DCS | AI | 4-20ma | 24Vdc |  | DCS Cabinet | 0 | 100 | %
P-OKITM07-335-08-PID-2001 | TM1401 | 33 | 003 |  | TM140133LV003 | TM140133LV003 | Dust Removal & Mist Removal | LEVEL CONTROL VALVE FOR SCRUBBER | LV | CONTROL VALVE | FIELD | DCS | AO | 4-20mA N.C. | 24Vdc |  | DCS Cabinet | 0 | 100 | %
P-OKITM07-336-08-PID-2001 | TM1401 | 33 | 002 |  | TM140133PS002 | TM140133PS002 | Dust Removal & Mist Removal | Pressure switch drip eliminator | PS | PRESSURE SWITCH | FIELD | DCS | DI | 24 VDC NO | 24Vdc |  | DCS Cabinet
P-OKITM07-336-08-PID-2001 | TM1401 | 33 | 002 |  | TM140133SV002 | TM140133SV002 | Dust Removal & Mist Removal | Cleaning water SOLENOID on valve | SV | Solenoid Valve | FIELD | DCS | DO | 24 VDC N.C. | 24Vdc |  | DCS Cabinet
P-OKITM07-336-08-PID-2001 | TM1401 | 33 | 002 |  | TM140133ZSC002 | TM140133ZSC002 | Dust Removal & Mist Removal | Cleaning water valve limit switch open | ZSC | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-336-08-PID-2001 | TM1401 | 33 | 002 |  | TM140133ZSO002 | TM140133ZSO002 | Dust Removal & Mist Removal | Cleaning water valve limit switch close | ZSO | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-336-08-PID-2001 | TM1401 | 33 | 010 |  | TM140133ZSO010 | TM140133ZSO010 | Dust Removal & Mist Removal | INDUCTIVE SENSOR | ZSO | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-336-08-PID-2001 | TM1401 | 33 | 010 |  | TM140133ZSC010 | TM140133ZSC010 | Dust Removal & Mist Removal | INDUCTIVE SENSOR | ZSC | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-336-08-PID-2001 | TM1401 | 33 | 011 |  | TM140133ZSO011 | TM140133ZSO011 | Dust Removal & Mist Removal | INDUCTIVE SENSOR | ZSO | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-336-08-PID-2001 | TM1401 | 33 | 011 |  | TM140133ZSC011 | TM140133ZSC011 | Dust Removal & Mist Removal | INDUCTIVE SENSOR | ZSC | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-336-08-PID-2001 | TM1401 | 33 | 020 |  | TM140133ZSO020 | TM140133ZSO020 | Dust Removal & Mist Removal | INDUCTIVE SENSOR | ZSO | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-336-08-PID-2001 | TM1401 | 33 | 020 |  | TM140133ZSC020 | TM140133ZSC020 | Dust Removal & Mist Removal | INDUCTIVE SENSOR | ZSC | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-336-08-PID-2001 | TM1401 | 33 | 021 |  | TM140133ZSO021 | TM140133ZSO021 | Dust Removal & Mist Removal | INDUCTIVE SENSOR | ZSO | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet
P-OKITM07-336-08-PID-2001 | TM1401 | 33 | 021 |  | TM140133ZSC021 | TM140133ZSC021 | Dust Removal & Mist Removal | INDUCTIVE SENSOR | ZSC | Limit Switch | Field | DCS | DI | FREE CONTACT N.O. | 24Vdc |  | DCS Cabinet

## SAFETY
PMT: | [5 empty] | EPC: |  |  |  | Project No. | P-OKITM08 | [6 empty] | DCS I/O Database
[8 empty] | LOGO & NAME |  | Project Name | OKITM Block 14
[10 empty] | Doc. No. | P-OKITM08-300-06-LST-2001 | [7 empty] | Abbreviations
Owner: | [5 empty] | Design Institute: |  |  |  | Rev. No. | 1 |  |  |  | Prep'd by |  |  |  | EER Electronic Equipment Room |  |  |  | SQRT Square Root
[8 empty] | LOGO & NAME |  | Purpose | REV |  |  |  | Chk'd by |  |  |  | CCR Control Center Room
[10 empty] | Date | 2021-04-01 |  |  |  | Appv'd by |  |  |  | ESP Electrostatic Precipitator
P&ID No. | Area |  | Loop No. | Suffix | Tag No. | DCS Tag Name | Process Area | Service Description | Signal Tag | Instrument Type | Location | System | IO Type | Signal |  |  | IO Loc. | PV LO | PV HI | Eng. Unit | Alarm | [6 empty] | State "0" | State "1" | CV Fail Action | CV Ctrl Action | PV CHAR | From |  | Cable |  |  | To |  | Rev. | Supply | Remarks
[14 empty] | Type | Power | Wire |  |  |  |  | LLL | LL | L | Nor. | H | HH | HHH | [5 empty] | JB/Panel No. | TB | Cable Number | Cable Type | Cable Order | Cabinet No. | TB |  | By
P-OKITM08-329-06-WRD-2042 | TM1402 | 31 | 501 | A | TM140231-HS-501A | TM140231HS501A | Dry End | REEL SAFETY - GATE #1 OPEN REQ | HS | Push button | TM140231-CB-101 | SAFETY | DI | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2042 | TM1402 | 31 | 501 | B | TM140231-HS-501B | TM140231HS501B | Dry End | REEL SAFETY - GATE #1 RESET REQ | HS | Push button | TM140231-CB-101 | SAFETY | DI | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2042 | TM1402 | 31 | 501 | A | TM140231-HSS-501A | TM140231HSS501A | Dry End | REEL SAFETY - E-STOP NO #1 | HSS | Emergency mushroom button | TM140231-CB-101 | SAFETY | DI | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2042 | TM1402 | 31 | 501 | B | TM140231-HSS-501B | TM140231HSS501B | Dry End | REEL SAFETY - E-STOP NO #2 | HSS | Emergency mushroom button | TM140231-CB-101 | SAFETY | DI | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2042 | TM1402 | 31 | 501 | A | TM140231-CX-501A | TM140231CX501A | Dry End | REEL SAFETY - GATE #1 - CLOSED CH1 | CX | Control relay contact | TM140231-SJB-501 | SAFETY | DI | dry contact, NC | 24Vdc
P-OKITM08-329-06-WRD-2042 | TM1402 | 31 | 501 | B | TM140231-CX-501B | TM140231CX501B | Dry End | REEL SAFETY - GATE #1 - CLOSED CH2 | CX | Control relay contact | TM140231-SJB-501 | SAFETY | DI | dry contact, NC | 24Vdc
P-OKITM08-329-06-WRD-2042 | TM1402 | 31 | 501 |  | TM140231-CR-501 | TM140231CR501 | Dry End | REEL SAFETY - GATE #1 - PERMISSION TO OPEN | CR | Control relay | TM140231-SJB-501 | SAFETY | DO | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2042 | TM1402 | 31 | 501 |  | TM140231-CX-501 | TM140231CX501 | Dry End | GATE #1 OPENED | CX | Control relay contact | TM140231-SJB-501 | SAFETY | DI | dry contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2042 | TM1402 | 31 | 501 | A | TM140231-XL-501A | TM140231XL501A | Dry End | REEL SAFETY - GATE #1 LIGHT TOWER - GREEN | XL | Lamp | TM140231-XL-501 | SAFETY | DO | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2042 | TM1402 | 31 | 501 | B | TM140231-XL-501B | TM140231XL501B | Dry End | REEL SAFETY - GATE #1 LIGHT TOWER - RED | XL | Lamp | TM140231-XL-501 | SAFETY | DO | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2043 | TM1402 | 31 | 502 | A | TM140231-HS-502A | TM140231HS502A | Dry End | GATE #2 - OPEN | HS | Push button | TM140231-CB-102 | SAFETY | DI | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2043 | TM1402 | 31 | 502 | B | TM140231-HS-502B | TM140231HS502B | Dry End | GATE #2 - RESET | HS | Push button | TM140231-CB-102 | SAFETY | DI | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2043 | TM1402 | 31 | 502 | A | TM140231-CX-502A | TM140231CX502A | Dry End | GATE #2 - CLOSED CH1 | CX | Control relay contact | TM140231-SJB-502 | SAFETY | DI | dry contact, NC | 24Vdc
P-OKITM08-329-06-WRD-2043 | TM1402 | 31 | 502 | B | TM140231-CX-502B | TM140231CX502B | Dry End | GATE #2 - CLOSED CH2 | CX | Control relay contact | TM140231-SJB-502 | SAFETY | DI | dry contact, NC | 24Vdc
P-OKITM08-329-06-WRD-2043 | TM1402 | 31 | 502 |  | TM140231-CR-502 | TM140231CR502 | Dry End | GATE #2 - PERMISSION TO OPEN | CR | Control relay | TM140231-SJB-502 | SAFETY | DO | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2043 | TM1402 | 31 | 502 |  | TM140231-CX-502 | TM140231CX502 | Dry End | GATE #2 OPENED | CX | Control relay contact | TM140231-SJB-502 | SAFETY | DI | dry contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2043 | TM1402 | 31 | 502 | A | TM140231-XL-502A | TM140231XL502A | Dry End | REEL SAFETY - GATE #2 LIGHT TOWER - GREEN | XL | Lamp | TM140231-XL-502 | SAFETY | DO | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2043 | TM1402 | 31 | 502 | B | TM140231-XL-502B | TM140231XL502B | Dry End | REEL SAFETY - GATE #2 LIGHT TOWER - RED | XL | Lamp | TM140231-XL-502 | SAFETY | DO | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2044 | TM1402 | 31 | 503 | A | TM140231-HS-503A | TM140231HS503A | Dry End | GATE #3 - OPEN | HS | Push button | TM140231-CB-103 | SAFETY | DI | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2044 | TM1402 | 31 | 503 | B | TM140231-HS-503B | TM140231HS503B | Dry End | GATE #3 - RESET | HS | Push button | TM140231-CB-103 | SAFETY | DI | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2044 | TM1402 | 31 | 503 | A | TM140231-CX-503A | TM140231CX503A | Dry End | GATE #3 - CLOSED CH1 | CX | Control relay contact | TM140231-SJB-503 | SAFETY | DI | dry contact, NC | 24Vdc
P-OKITM08-329-06-WRD-2044 | TM1402 | 31 | 503 | B | TM140231-CX-503B | TM140231CX503B | Dry End | GATE #3 - CLOSED CH2 | CX | Control relay contact | TM140231-SJB-503 | SAFETY | DI | dry contact, NC | 24Vdc
P-OKITM08-329-06-WRD-2044 | TM1402 | 31 | 503 |  | TM140231-CR-503 | TM140231CR503 | Dry End | GATE #3 - PERMISSION TO OPEN | CR | Control relay | TM140231-SJB-503 | SAFETY | DO | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2044 | TM1402 | 31 | 503 |  | TM140231-CX-503 | TM140231CX503 | Dry End | GATE #3 OPENED | CX | Control relay contact | TM140231-SJB-503 | SAFETY | DI | dry contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2044 | TM1402 | 31 | 503 | A | TM140231-XL-503A | TM140231XL503A | Dry End | REEL SAFETY - GATE #3 LIGHT TOWER - GREEN | XL | Lamp | TM140231-XL-503 | SAFETY | DO | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2044 | TM1402 | 31 | 503 | B | TM140231-XL-503B | TM140231XL503B | Dry End | REEL SAFETY - GATE #3 LIGHT TOWER - RED | XL | Lamp | TM140231-XL-503 | SAFETY | DO | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2048 | TM1402 | 31 | 505 | A | TM140231-GSE-505A | TM140231GSE505A | Dry End | REEL SAFETY - REEL FRAMEWORK GATES - PIN INSERTED FS | GSE | Safety Limit Switch Element | TM140231-JB-460 | SAFETY | DI | wet contact, NC | 24Vdc
P-OKITM08-329-06-WRD-2048 | TM1402 | 31 | 505 | B | TM140231-GSE-505B | TM140231GSE505B | Dry End | REEL SAFETY - REEL FRAMEWORK GATES - PIN INSERTED BS | GSE | Safety Limit Switch Element | TM140231-JB-860 | SAFETY | DI | wet contact, NC | 24Vdc
P-OKITM08-329-06-WRD-2045 | TM1402 | 31 | 543 | A | TM140231-ESV-543A | TM140231ESV543A | Dry End | REEL SAFETY - SECURE S.A. EJECT | ESV | Safety Solenoid Valve | TM140231-SJB-001 | SAFETY | DO | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2045 | TM1402 | 31 | 543 | B | TM140231-ESV-543B | TM140231ESV543B | Dry End | REEL SAFETY - SECURE S.A. EJECT | ESV | Safety Solenoid Valve | TM140231-SJB-001 | SAFETY | DO | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2045 | TM1402 | 31 | 543 |  | TM140231-GSE-543 | TM140231GSE543 | Dry End | REEL SAFETY - SECURE S.A. EJECT LIMIT SWITCH | GSE | Safety Limit Switch Element | TM140231-SJB-001 | SAFETY | DI | wet contact, NC | 24Vdc
P-OKITM08-329-06-WRD-2049 | TM1402 | 31 | 555 |  | TM140231-CR-555 | TM140231CR555 | Dry End | REEL SAFETY - REEL DRUM MOTOR STOP CMD | CR | Control relay | TM140249-CB-500 | SAFETY | DO | wet contact, NO | 24Vdc | [26 empty] | Stop Category 1 EN IEC 61800-5-2
P-OKITM08-329-06-WRD-2045 | TM1402 | 31 | 560 | A | TM140231-ESV-560A | TM140231ESV560A | Dry End | REEL SAFETY - SECURE MANIFOLD PM3 | ESV | Safety Solenoid Valve | TM140231-SJB-001 | SAFETY | DO | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2045 | TM1402 | 31 | 560 | B | TM140231-ESV-560B | TM140231ESV560B | Dry End | REEL SAFETY - SECURE MANIFOLD PM3 | ESV | Safety Solenoid Valve | TM140231-SJB-001 | SAFETY | DO | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2045 | TM1402 | 31 | 560 |  | TM140231-GSE-560 | TM140231GSE560 | Dry End | REEL SAFETY - SECURE MANIFOLD PM3 LIMIT SWITCH | GSE | Safety Limit Switch Element | TM140231-SJB-001 | SAFETY | DI | wet contact, NC | 24Vdc
P-OKITM08-329-06-WRD-2046 | TM1402 | 34 | 645 | A | TM140234-ESV-645A | TM140234ESV645A | Dry End | REEL SAFETY - WEIGHT STATION ARMS BLOCKED - SAFETY VALVE #1 | ESV | Safety Solenoid Valve | TM140134-HB-002 | SAFETY | DO | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2046 | TM1402 | 34 | 645 | B | TM140234-ESV-645B | TM140234ESV645B | Dry End | REEL SAFETY - WEIGHT STATION ARMS BLOCKED - SAFETY VALVE #2 | ESV | Safety Solenoid Valve | TM140134-HB-002 | SAFETY | DO | wet contact, NO | 24Vdc
P-OKITM08-329-06-WRD-2046 | TM1402 | 34 | 645 | A | TM140234-GSE-645A | TM140234GSE645A | Dry End | REEL SAFETY - WEIGHT STATION ARMS STOPED - SAFETY LIMIT SWITCH #1 | GSE | Safety Limit Switch Element | TM140134-HB-002 | SAFETY | DI | wet contact, NC | 24Vdc
P-OKITM08-329-06-WRD-2046 | TM1402 | 34 | 645 | B | TM140234-GSE-645B | TM140234GSE645B | Dry End | REEL SAFETY - WEIGHT STATION ARMS STOPED - SAFETY LIMIT SWITCH #2 | GSE | Safety Limit Switch Element | TM140134-HB-002 | SAFETY | DI | wet contact, NC | 24Vdc
P-OKITM08-329-06-WRD-2047 | TM1402 | 31 | 643 |  | TM140231-GSE-643 | TM140231GSE643 | Dry End | POPE REEL SECONDARY ARMS - PERMISSION GATE | GSE | Safety Limit Switch Element | TM140231-JB-160 | SAFETY | DI | wet contact, NC | 24Vdc
P-OKITM08-329-06-WRD-2048 | TM1402 | 31 | 648 | A | TM140231-GSE-648A | TM140231GSE648A | Dry End | POPE REEL WEIGHT STATION ARM LOWERED FS | GSE | Safety Limit Switch Element | TM140231-JB-460 | SAFETY | DI | wet contact, NC | 24Vdc
P-OKITM08-329-06-WRD-2048 | TM1402 | 31 | 648 | B | TM140231-GSE-648B | TM140231GSE648B | Dry End | POPE REEL WEIGHT STATION ARM LOWERED BS | GSE | Safety Limit Switch Element | TM140231-JB-860 | SAFETY | DI | wet contact, NC | 24Vdc
P-OKITM08-329-06-WRD-2047 | TM1402 | 31 | 654 | A | TM140231-GSE-654A | TM140231GSE654A | Dry End | POPE REEL SPOOL STORAGE LOADED FS | GSE | Safety Limit Switch Element | TM140231-JB-360 | SAFETY | DI | wet contact, NC | 24Vdc
P-OKITM08-329-06-WRD-2047 | TM1402 | 31 | 654 | B | TM140231-GSE-654B | TM140231GSE654B | Dry End | POPE REEL SPOOL STORAGE LOADED BS | GSE | Safety Limit Switch Element | TM140231-JB-760 | SAFETY | DI | wet contact, NC | 24Vdc
P-OKITM08-329-06-WRD-2047 | TM1402 | 31 | 677 | C | TM140231-GSE-677C | TM140231GSE677C | Dry End | POPE REEL SPOOL BRAKE ARMS LOWERED FS | GSE | Safety Limit Switch Element | TM140231-JB-360 | SAFETY | DI | wet contact, NC | 24Vdc
P-OKITM08-329-06-WRD-2047 | TM1402 | 31 | 677 | D | TM140231-GSE-677D | TM140231GSE677D | Dry End | POPE REEL SPOOL BRAKE ARMS LOWERED BS | GSE | Safety Limit Switch Element | TM140231-JB-760 | SAFETY | DI | wet contact, NC | 24Vdc

## Signal Exchange List
PMT: | [6 empty] | EPC: |  |  |  |  | Project No. | P-OKITM08 | [6 empty] | DCS I/O Database
[12 empty] | Project Name | OKITM Block 14
[12 empty] | Doc. No. | P-OKITM08-300-06-LST-2001 | [7 empty] | Abbreviations
Owner: | [6 empty] | Design Institute: |  |  |  |  | Rev. No. | 1 |  |  |  | Prep'd by | R. Krupa |  |  | EER Electronic Equipment Room |  |  |  | SQRT Square Root
[12 empty] | Purpose | REV |  |  |  | Chk'd by |  |  |  | CCR Control Center Room
[12 empty] | Date | 2021-04-01 |  |  |  | Appv'd by |  |  |  | ESP Electrostatic Precipitator
P&ID No. | Area |  | Loop No. | Suffix |  | DEVICE Tag No. | DCS Tag Name | REMARKS | Process Area | Service Description | Signal Tag | Instrument Type | Location | System | IO Type | Signal |  |  | IO Loc. | PV LO | PV HI | Eng. Unit | Alarm | [6 empty] | State "0" | State "1" | CV Fail Action | CV Ctrl Action | PV CHAR | From |  | Cable |  |  | To |  | Rev. | Supply | Remarks
[16 empty] | Type | Power | Wire |  |  |  |  | LLL | LL | L | Nor. | H | HH | HHH | [5 empty] | JB/Panel No. | TB | Cable Number | Cable Type | Cable Order | Cabinet No. | TB |  | By
| TM1402 | 30 | 665 |  | STRF | TM140230M0665 | TM140230M665_STRF |  | Wet End | HEADBOX LIP ADJUSTMENT MOTOR - OPEN | M | Start forward signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 665 |  | STRR | TM140230M0665 | TM140230M665_STRR |  | Wet End | HEADBOX LIP ADJUSTMENT MOTOR - CLOSE | M | Start reverse signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 665 |  | RY | TM140230M0665 | TM140230M665_RY |  | Wet End | HEADBOX LIP ADJUSTMENT MOTOR - READY | M | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 665 |  | FWDR | TM140230M0665 | TM140230M665_FWDR |  | Wet End | HEADBOX LIP ADJUSTMENT MOTOR - OPEN FEEDBACK | M | Run feedback forward signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 665 |  | REVR | TM140230M0665 | TM140230M665_REVR |  | Wet End | HEADBOX LIP ADJUSTMENT MOTOR - CLOSE FEEDBACK | M | Run feedback reverse signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 423 |  | STR | TM140230M4233 | TM140230M423_STR |  | Wet End | FORMER BREAST ROLL DOCTOR OSCILLATION MOTOR - START | M | Start/Stop signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 423 |  | RY | TM140230M4233 | TM140230M423_RY |  | Wet End | FORMER BREAST ROLL DOCTOR OSCILLATION MOTOR - READY | M | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 423 |  | RF | TM140230M4233 | TM140230M423_RF |  | Wet End | FORMER BREAST ROLL DOCTOR OSCILLATION MOTOR - FEEDBACK | M | Run feedback signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 424 |  | STR | TM140234M4234 | TM140230M424_STR |  | Wet End | FORMING ROLL DOCTOR OSCILLATION MOTOR - START | M | Start/Stop signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 424 |  | RY | TM140234M4234 | TM140230M424_RY |  | Wet End | FORMING ROLL DOCTOR OSCILLATION MOTOR - READY | M | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 424 |  | RF | TM140234M4234 | TM140230M424_RF |  | Wet End | FORMING ROLL DOCTOR OSCILLATION MOTOR - FEEDBACK | M | Run feedback signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 425 |  | STR | TM140234M4235 | TM140230M425_STR |  | Wet End | FORMER GUIDE ROLL DOCTOR OSCILLATION MOTOR - START | M | Start/Stop signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 425 |  | RY | TM140234M4235 | TM140230M425_RY |  | Wet End | FORMER GUIDE ROLL DOCTOR OSCILLATION MOTOR - READY | M | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 425 |  | RF | TM140234M4235 | TM140230M425_RF |  | Wet End | FORMER GUIDE ROLL DOCTOR OSCILLATION MOTOR - FEEDBACK | M | Run feedback signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 426 |  | STR | TM140234M4236 | TM140230M426_STR |  | Wet End | FORMER LEAD ROLL DOCTOR OSCILLATION MOTOR - START | M | Start/Stop signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 426 |  | RY | TM140234M4236 | TM140230M426_RY |  | Wet End | FORMER LEAD ROLL DOCTOR OSCILLATION MOTOR - READY | M | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 426 |  | RF | TM140234M4236 | TM140230M426_RF |  | Wet End | FORMER LEAD ROLL DOCTOR OSCILLATION MOTOR - FEEDBACK | M | Run feedback signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 455 |  | STRF | TM140230M4255 | TM140230M455_STRF |  | Wet End | WIRE BREAST ROLL LIFT MOTOR - LIFT | M | Start forward signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 455 |  | STRR | TM140230M4255 | TM140230M455_STRR |  | Wet End | WIRE BREAST ROLL LIFT MOTOR - LOWER | M | Start reverse signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 455 |  | RY | TM140230M4255 | TM140230M455_RY |  | Wet End | WIRE BREAST ROLL LIFT MOTOR - READY | M | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 455 |  | FWDR | TM140230M4255 | TM140230M455_FWDR |  | Wet End | WIRE BREAST ROLL LIFT MOTOR - LIFT FEEDBACK | M | Run feedback forward signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 455 |  | REVR | TM140230M4255 | TM140230M455_REVR |  | Wet End | WIRE BREAST ROLL LIFT MOTOR - LOWER FEEDBACK | M | Run feedback reverse signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 463 |  | STRF | TM140230M4263 | TM140230M463_STRF |  | Wet End | WIRE STRETCHER MOTOR - STRETCH | M | Start forward signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 463 |  | STRR | TM140230M4263 | TM140230M463_STRR |  | Wet End | WIRE STRETCHER MOTOR - LOOSEN | M | Start reverse signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 463 |  | RY | TM140230M4263 | TM140230M463_RY |  | Wet End | WIRE STRETCHER MOTOR - READY | M | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 463 |  | FWDR | TM140230M4263 | TM140230M463_FWDR |  | Wet End | WIRE STRETCHER MOTOR - STRETCH FEEDBACK | M | Run feedback forward signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 463 |  | REVR | TM140230M4263 | TM140230M463_REVR |  | Wet End | WIRE STRETCHER MOTOR - LOOSEN FEEDBACK | M | Run feedback reverse signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 334 | A | STR | TM140230M0334A | TM140230M334A_STR |  | Wet End | FELT ROLL #1 DOCTOR OSCILLATION MOTOR - START | M | Start/Stop signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 334 | A | RY | TM140230M0334A | TM140230M334A_RY |  | Wet End | FELT ROLL #1 DOCTOR OSCILLATION MOTOR - READY | M | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 334 | A | RF | TM140230M0334A | TM140230M334A_RF |  | Wet End | FELT ROLL #1 DOCTOR OSCILLATION MOTOR - FEEDBACK | M | Run feedback signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 334 | B | STR | TM140230M0334B | TM140230M334B_STR |  | Wet End | FELT ROLL #2 DOCTOR OSCILLATION MOTOR - START | M | Start/Stop signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 334 | B | RY | TM140230M0334B | TM140230M334B_RY |  | Wet End | FELT ROLL #2 DOCTOR OSCILLATION MOTOR - READY | M | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 334 | B | RF | TM140230M0334B | TM140230M334B_RF |  | Wet End | FELT ROLL #2 DOCTOR OSCILLATION MOTOR - FEEDBACK | M | Run feedback signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 350 |  | STRF | TM140230M0320 | TM140230M350_STRF |  | Wet End | FELT STRETCHER MOTOR - STRETCH | M | Start forward signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 350 |  | STRR | TM140230M0320 | TM140230M350_STRR |  | Wet End | FELT STRETCHER MOTOR - LOOSEN | M | Start reverse signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 350 |  | RY | TM140230M0320 | TM140230M350_RY |  | Wet End | FELT STRETCHER MOTOR - READY | M | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 350 |  | FWDR | TM140230M0320 | TM140230M350_FWDR |  | Wet End | FELT STRETCHER MOTOR - STRETCH FEEDBACK | M | Run feedback forward signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 30 | 350 |  | REVR | TM140230M0320 | TM140230M350_REVR |  | Wet End | FELT STRETCHER MOTOR - LOOSEN FEEDBACK | M | Run feedback reverse signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 31 | 215 |  | STR | TM140231M2611 | TM140231M215_STR |  | Dry End | YANKEE DRYER CLEANING DOCTOR OSCILLATION MOTOR - START | M | Start/Stop signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 31 | 215 |  | RY | TM140231M2611 | TM140231M215_RY |  | Dry End | YANKEE DRYER CLEANING DOCTOR OSCILLATION MOTOR - READY | M | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 31 | 215 |  | RF | TM140231M2611 | TM140231M215_RF |  | Dry End | YANKEE DRYER CLEANING DOCTOR OSCILLATION MOTOR - FEEDBACK | M | Run feedback signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 31 | 225 |  | STR | TM140231M2622 | TM140231M225_STR |  | Dry End | YANKEE DRYER CREPING DOCTOR OSCILLATION MOTOR - START | M | Start/Stop signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 31 | 225 |  | RY | TM140231M2622 | TM140231M225_RY |  | Dry End | YANKEE DRYER CREPING DOCTOR OSCILLATION MOTOR - READY | M | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 31 | 225 |  | RF | TM140231M2622 | TM140231M225_RF |  | Dry End | YANKEE DRYER CREPING DOCTOR OSCILLATION MOTOR - FEEDBACK | M | Run feedback signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 31 | 235 |  | STR | TM140231M2632 | TM140231M235_STR |  | Dry End | YANKEE DRYER CUT-OFF DOCTOR OSCILLATION MOTOR - START | M | Start/Stop signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 31 | 235 |  | RY | TM140231M2632 | TM140231M235_RY |  | Dry End | YANKEE DRYER CUT-OFF DOCTOR OSCILLATION MOTOR - READY | M | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 31 | 235 |  | RF | TM140231M2632 | TM140231M235_RF |  | Dry End | YANKEE DRYER CUT-OFF DOCTOR OSCILLATION MOTOR - FEEDBACK | M | Run feedback signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 31 | 781 |  | STRF | TM140231M7581 | TM140231M781_STRF |  | Dry End | THREADING SYS TAIL CUTTER MOTOR - NARROW | M | Start forward signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 31 | 781 |  | STRR | TM140231M7581 | TM140231M781_STRR |  | Dry End | THREADING SYS TAIL CUTTER MOTOR - WIDEN | M | Start reverse signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 31 | 781 |  | RY | TM140231M7581 | TM140231M781_RY |  | Dry End | THREADING SYS TAIL CUTTER MOTOR - READY | M | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 31 | 781 |  | FWDR | TM140231M7581 | TM140231M781_FWDR |  | Dry End | THREADING SYS TAIL CUTTER MOTOR - NARROW FEEDBACK | M | Run feedback forward signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 31 | 781 |  | REVR | TM140231M7581 | TM140231M781_REVR |  | Dry End | THREADING SYS TAIL CUTTER MOTOR - WIDEN FEEDBACK | M | Run feedback reverse signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 31 | 781 |  | SI | TM140231M7581 | TM140231M781_SI |  | Dry End | THREADING SYS TAIL CUTTER MOTOR - SPEED | M | Speed signal (rpm) | MCC | DCS | AI | 4-20ma | profibus |  | DCS Cabinet
| TM1402 | 31 | 781 |  | SPC | TM140231M7581 | TM140231M781_SPC |  | Dry End | THREADING SYS TAIL CUTTER MOTOR - SPEED SETPOINT | M | Speed setpoint signal (rpm) | MCC | DCS | AO | 4-20ma | profibus |  | DCS Cabinet
| TM1402 | 34 | 101 | A | STR | TM140234M1001A | TM140234M101A_STR |  | Lubrication, Hydraulic system | LUBRICATION UNIT FEED PUMP#1 MOTOR - START | M | Start/Stop signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 34 | 101 | A | RY | TM140234M1001A | TM140234M101A_RY |  | Lubrication, Hydraulic system | LUBRICATION UNIT FEED PUMP#1 MOTOR - READY | M | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 34 | 101 | A | RF | TM140234M1001A | TM140234M101A_RF |  | Lubrication, Hydraulic system | LUBRICATION UNIT FEED PUMP#1 MOTOR - FEEDBACK | M | Run feedback signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 34 | 101 | B | STR | TM140234M1001B | TM140234M101B_STR |  | Lubrication, Hydraulic system | LUBRICATION UNIT FEED PUMP#2 MOTOR - START | M | Start/Stop signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 34 | 101 | B | RY | TM140234M1001B | TM140234M101B_RY |  | Lubrication, Hydraulic system | LUBRICATION UNIT FEED PUMP#2 MOTOR - READY | M | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 34 | 101 | B | RF | TM140234M1001B | TM140234M101B_RF |  | Lubrication, Hydraulic system | LUBRICATION UNIT FEED PUMP#2 MOTOR - FEEDBACK | M | Run feedback signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 34 | 102 |  | STR | TM140234H1032 | TM140234H102_STR |  | Lubrication, Hydraulic system | LUBRICATION UNIT TANK HEATER - ON | H | Start/Stop signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 34 | 102 |  | RY | TM140234H1032 | TM140234H102_RY |  | Lubrication, Hydraulic system | LUBRICATION UNIT TANK HEATER - READY | H | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 34 | 102 |  | RF | TM140234H1032 | TM140234H102_RF |  | Lubrication, Hydraulic system | LUBRICATION UNIT TANK HEATER - FEEDBACK | H | Run feedback signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 34 | 801 | A | STR | TM140234M8801A | TM140234M801A_STR |  | Lubrication, Hydraulic system | HYDRAULIC UNIT PUMP#1 MOTOR - START | M | Start/Stop signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 34 | 801 | A | RY | TM140234M8801A | TM140234M801A_RY |  | Lubrication, Hydraulic system | HYDRAULIC UNIT PUMP#1 MOTOR - READY | M | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 34 | 801 | A | RF | TM140234M8801A | TM140234M801A_RF |  | Lubrication, Hydraulic system | HYDRAULIC UNIT PUMP#1 MOTOR - FEEDBACK | M | Run feedback signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 34 | 801 | B | STR | TM140234M8801B | TM140234M801B_STR |  | Lubrication, Hydraulic system | HYDRAULIC UNIT PUMP#2 MOTOR - START | M | Start/Stop signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 34 | 801 | B | RY | TM140234M8801B | TM140234M801B_RY |  | Lubrication, Hydraulic system | HYDRAULIC UNIT PUMP#2 MOTOR - READY | M | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 34 | 801 | B | RF | TM140234M8801B | TM140234M801B_RF |  | Lubrication, Hydraulic system | HYDRAULIC UNIT PUMP#2 MOTOR - FEEDBACK | M | Run feedback signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 34 | 802 |  | STR | TM140234H8832 | TM140234M802_STR |  | Lubrication, Hydraulic system | HYDRAULIC UNIT HEATER - START | M | Start/Stop signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 34 | 802 |  | RY | TM140234H8832 | TM140234M802_RY |  | Lubrication, Hydraulic system | HYDRAULIC UNIT HEATER - READY | M | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 34 | 802 |  | RF | TM140234H8832 | TM140234M802_RF |  | Lubrication, Hydraulic system | HYDRAULIC UNIT HEATER - FEEDBACK | M | Run feedback signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 34 | 803 |  | STR | TM140234M8803 | TM140234M803_STR |  | Lubrication, Hydraulic system | HYDRAULIC UNIT RECIRCULATION PUMP - START | M | Start/Stop signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
| TM1402 | 34 | 803 |  | RY | TM140234M8803 | TM140234M803_RY |  | Lubrication, Hydraulic system | HYDRAULIC UNIT RECIRCULATION PUMP - READY | M | Ready signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
| TM1402 | 34 | 803 |  | RF | TM140234M8803 | TM140234M803_RF |  | Lubrication, Hydraulic system | HYDRAULIC UNIT RECIRCULATION PUMP - FEEDBACK | M | Run feedback signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 001 | M1 | STR | TM140232F0001M1 | TM140232F001M1_STR |  | Burner & Hood System | RECIRCULATING WE Air Fan START | F | Start/Stop signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 001 | M1 | RF | TM140232F0001M1 | TM140232F001M1_RF |  | Burner & Hood System | RECIRCULATING WE Air Fan FORWARD FEEDBACK | F | Run feedback signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 001 | M1 | AL | TM140232F0001M1 | TM140232F001M1_AL |  | Burner & Hood System | RECIRCULATING WE Air Fan FAN ALARM | F | Alarm Signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 001 | M1 | RY | TM140232F0001M1 | TM140232F001M1_RY |  | Burner & Hood System | RECIRCULATING WE Air Fan READY TO START | F | Ready signal | MCC | DCS | DI | NO | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 001 | M1 | CURR | TM140232F0001M1 | TM140232F001M1_CURR |  | Burner & Hood System | RECIRCULATING WE Air Fan CURRENT | F | Current absorption Signal | MCC | DCS | AI | 4-20ma | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 001 | M1 | SPC | TM140232F0001M1 | TM140232F001M1_SPC |  | Burner & Hood System | RECIRCULATING WE Air Fan SPEED REFERENCE | F | Speed Setpoint Signal | MCC | DCS | AO | 4-20ma | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 002 | M1 | STR | TM140232F0002M1 | TM140232F002M1_STR |  | Burner & Hood System | RECIRCULATING DE Air Fan START | F | Start/Stop signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 002 | M1 | RF | TM140232F0002M1 | TM140232F002M1_RF |  | Burner & Hood System | RECIRCULATING DE Air Fan FORWARD FEEDBACK | F | Run feedback signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 002 | M1 | AL | TM140232F0002M1 | TM140232F002M1_AL |  | Burner & Hood System | RECIRCULATING DE Air Fan FAN ALARM | F | Alarm Signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 002 | M1 | RY | TM140232F0002M1 | TM140232F002M1_RY |  | Burner & Hood System | RECIRCULATING DE Air Fan READY TO START | F | Ready signal | MCC | DCS | DI | NO | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 002 | M1 | CURR | TM140232F0002M1 | TM140232F002M1_CURR |  | Burner & Hood System | RECIRCULATING DE Air Fan CURRENT | F | Current absorption Signal | MCC | DCS | AI | 4-20ma | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 002 | M1 | SPC | TM140232F0002M1 | TM140232F002M1_SPC |  | Burner & Hood System | RECIRCULATING DE Air Fan SPEED REFFERENCE | F | Speed Setpoint Signal | MCC | DCS | AO | 4-20ma | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 004 | M1 | STR | TM140232F0004M1 | TM140232F004M1_STR |  | Burner & Hood System | EXHAUST Air Fan START | F | Start/Stop signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 004 | M1 | RF | TM140232F0004M1 | TM140232F004M1_RF |  | Burner & Hood System | EXHAUST Air Fan FORWARD FEEDBACK | F | Run feedback signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 004 | M1 | AL | TM140232F0004M1 | TM140232F004M1_AL |  | Burner & Hood System | EXHAUST Air Fan FAN ALARM | F | Alarm signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 004 | M1 | RY | TM140232F0004M1 | TM140232F004M1_RY |  | Burner & Hood System | EXHAUST Air Fan READY TO START | F | Ready signal | MCC | DCS | DI | NO | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 004 | M1 | CURR | TM140232F0004M1 | TM140232F004M1_CURR |  | Burner & Hood System | EXHAUST Air Fan CURRENT | F | Current absorption Signal | MCC | DCS | AI | 4-20ma | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 004 | M1 | SPC | TM140232F0004M1 | TM140232F004M1_SPC |  | Burner & Hood System | EXHAUST Air Fan SPEED REFERENCE | F | Speed Setpoint Signal | MCC | DCS | AO | 4-20ma | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 003 | M1 | STR | TM140232F0003M1 | TM140232F003M1_STR |  | Burner & Hood System | MAKE UP Air Fan START | F | Start/Stop signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 003 | M1 | RF | TM140232F0003M1 | TM140232F003M1_RF |  | Burner & Hood System | MAKE UP Air Fan FORWARD FEEDBACK | F | Run feedback signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 003 | M1 | AL | TM140232F0003M1 | TM140232F003M1_AL |  | Burner & Hood System | MAKE UP Air Fan FAN ALARM | F | Alarm signa | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 003 | M1 | RY | TM140232F0003M1 | TM140232F003M1_RY |  | Burner & Hood System | MAKE UP Air Fan READY TO START | F | Ready signal | MCC | DCS | DI | NO | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 003 | M1 | CURR | TM140232F0003M1 | TM140232F003M1_CURR |  | Burner & Hood System | MAKE UP Air Fan CURRENT | F | Current absorption Signal | MCC | DCS | AI | 4-20ma | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 003 | M1 | SPC | TM140232F0003M1 | TM140232F003M1_SPC |  | Burner & Hood System | MAKE UP Air Fan SPEED REFERENCE | F | Speed Setpoint Signal | MCC | DCS | AO | 4-20ma | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 006 | M1 | STR-UP | TM140232D0006M1 | TM140232D006M1_STR-UP |  | Burner & Hood System | MOTOR-REDUCER for WE Hood OPEN/CLOSE UP STROKE | D | Run forward signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 006 | M1 | STR-DOWN | TM140232D0006M1 | TM140232D006M1_STR-DOWN |  | Burner & Hood System | MOTOR-REDUCER for WE Hood OPEN/CLOSE DOWN STROKE | D | Run reverse signal | MCC | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 006 | M1 | AL | TM140232D0006M1 | TM140232D006M1_AL |  | Burner & Hood System | MOTOR-REDUCER for WE Hood OPEN/CLOSE Emergency Signal | D | Emergency Signal | MCC | DCS | DI | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 011 | M1 | STR-UP | TM140232D0011M1 | TM140232D011M1_STR-UP |  | Burner & Hood System | MOTOR-REDUCER for DE Hood OPEN/CLOSE UP STROKE | D | Run forward signal | MCC | DCS | DO | N.O. | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 011 | M1 | STR-DOWN | TM140232D0011M1 | TM140232D011M1_STR-DOWN |  | Burner & Hood System | MOTOR-REDUCER for DE Hood OPEN/CLOSE DOWN STROKE | D | Run reverse signal | MCC | DCS | DO | N.O. | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2001 | TM1402 | 32 | 011 | M1 | AL | TM140232D0011M1 | TM140232D011M1_AL |  | Burner & Hood System | MOTOR-REDUCER forDE Hood OPEN/CLOSE Emergency Signal | D | Emergency Signal | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 005 | AM1 | STR-UP | TM140232D005 | TM140232D005AM1_STR-UP |  | Burner & Hood System | MOTOR-REDUCER for WE FILTER In / Out UP STROKE | D | Run forward signal | FIELD | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 005 | AM1 | STR-DOWN | TM140232D005 | TM140232D005AM1_STR-DOWN |  | Burner & Hood System | MOTOR-REDUCER for WE FILTER In / Out DOWN STROKE | D | Run reverse signal | FIELD | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 005 | AM1 | AL | TM140232D005 | TM140232D005AM1_AL |  | Burner & Hood System | MOTOR-REDUCER for WE FILTER In / Out UPSTROKE EMERGENCY SIGNAL | D | Emergency Signal | FIELD | DCS | DI | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 005 | BM1 | STR-UP | TM140232Run forward signal005 | TM140232D005BM1_STR-UP |  | Burner & Hood System | MOTOR-REDUCER for WE FILTER In / Out OPEN STROKE | D | Run forward signal | FIELD | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 005 | BM1 | STR-DOWN | TM140232Run reverse signal005 | TM140232D005BM1_STR-DOWN |  | Burner & Hood System | MOTOR-REDUCER for WE FILTER In / Out CLOSE STROKE | D | Run reverse signal | FIELD | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 005 | BM1 | AL | TM140232Emergency Signal005 | TM140232D005BM1_AL |  | Burner & Hood System | MOTOR-REDUCER for WE FILTER In / Out EMERGENCY SIGNAL | D | Emergency Signal | FIELD | DCS | DI | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 005 | CM1 | STR-UP | TM140232Run forward signal005 | TM140232D005CM1_STR-UP |  | Burner & Hood System | MOTOR-REDUCER for WE FILTER In / Out OPEN STROKE | D | Run forward signal | FIELD | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 005 | CM1 | STR-DOWN | TM140232Run reverse signal005 | TM140232D005CM1_STR-DOWN |  | Burner & Hood System | MOTOR-REDUCER for WE FILTER In / Out CLOSE STROKE | D | Run reverse signal | FIELD | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 005 | CM1 | AL | TM140232Emergency Signal005 | TM140232D005CM1_AL |  | Burner & Hood System | MOTOR-REDUCER for WE FILTER In / Out EMERGENCY SIGNAL | D | Emergency Signal | FIELD | DCS | DI | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 005 | DM1 | STR-UP | TM140232DO005 | TM140232D005DM1_STR-UP |  | Burner & Hood System | MOTOR-REDUCER for WE FILTER In / Out OPEN STROKE | D | Run forward signal | FIELD | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 005 | DM1 | STR-DOWN | TM140232DO005 | TM140232D005DM1_STR-DOWN |  | Burner & Hood System | MOTOR-REDUCER for WE FILTER In / Out CLOSE STROKE | D | Run reverse signal | FIELD | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 005 | DM1 | AL | TM140232DI005 | TM140232D005DM1_AL |  | Burner & Hood System | MOTOR-REDUCER for WE FILTER In / Out EMERGENCY SIGNAL | D | Emergency Signal | FIELD | DCS | DI | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 006 | AM1 | STR-UP | TM140232DO006 | TM140232D006AM1_STR-UP |  | Burner & Hood System | MOTOR-REDUCER for DE FILTER In / Out OPEN STROKE | D | Run forward signal | FIELD | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 006 | AM1 | STR-DOWN | TM140232DO006 | TM140232D006AM1_STR-DOWN |  | Burner & Hood System | MOTOR-REDUCER for DE FILTER In / Out CLOSE STROKE | D | Run reverse signal | FIELD | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 006 | AM1 | AL | TM140232DI006 | TM140232D006AM1_AL |  | Burner & Hood System | MOTOR-REDUCER for DE FILTER In / Out EMERGENCY SIGNAL | D | Emergency Signal | FIELD | DCS | DI | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 006 | BM1 | STR-UP | TM140232DO006 | TM140232D006BM1_STR-UP |  | Burner & Hood System | MOTOR-REDUCER for DE FILTER In / Out OPEN STROKE | D | Run forward signal | FIELD | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 006 | BM1 | STR-DOWN | TM140232DO006 | TM140232D006BM1_STR-DOWN |  | Burner & Hood System | MOTOR-REDUCER for DE FILTER In / Out CLOSE STROKE | D | Run reverse signal | FIELD | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 006 | BM1 | AL | TM140232DI006 | TM140232D006BM1_AL |  | Burner & Hood System | MOTOR-REDUCER for DE FILTER In / Out EMERGENCY SIGNAL | D | Emergency Signal | FIELD | DCS | DI | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 006 | CM1 | STR-UP | TM140232DO006 | TM140232D006CM1_STR-UP |  | Burner & Hood System | MOTOR-REDUCER for DE FILTER In / Out OPEN STROKE | D | Run forward signal | FIELD | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 006 | CM1 | STR-DOWN | TM140232DO006 | TM140232D006CM1_STR-DOWN |  | Burner & Hood System | MOTOR-REDUCER for DE FILTER In / Out CLOSE STROKE | D | Run reverse signal | FIELD | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 006 | CM1 | AL | TM140232DI006 | TM140232D006CM1_AL |  | Burner & Hood System | MOTOR-REDUCER for DE FILTER In / Out EMERGENCY SIGNAL | D | Emergency Signal | FIELD | DCS | DI | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 006 | DM1 | STR-UP | TM140232DO006 | TM140232D006DM1_STR-UP |  | Burner & Hood System | MOTOR-REDUCER for DE FILTER In / Out OPEN STROKE | D | Run forward signal | FIELD | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 006 | DM1 | STR-DOWN | TM140232DO006 | TM140232D006DM1_STR-DOWN |  | Burner & Hood System | MOTOR-REDUCER for DE FILTER In / Out CLOSE STROKE | D | Run reverse signal | FIELD | DCS | DO | N.O | profibus |  | DCS Cabinet
P-OKITM08-325-08-PID-2002 | TM1402 | 32 | 006 | DM1 | AL | TM140232DI006 | TM140232D006DM1_AL |  | Burner & Hood System | MOTOR-REDUCER for DE FILTER In / Out EMERGENCY SIGNAL | D | Emergency Signal | FIELD | DCS | DI | N.O | profibus |  | DCS Cabinet
P-OKITM08-324-08-PID-2001 | TM1402 | 35 | 001 | M1 | STR | TM140235U0001M1 | TM140235U001M1_STR |  | Steam & Condensate | CP PUMP START | U | Start/Stop signal | MCC | DCS | DO | N.O. | profibus |  | DCS Cabinet
P-OKITM08-324-08-PID-2001 | TM1402 | 35 | 001 | M1 | RF | TM140235U0001M1 | TM140235U001M1_RF |  | Steam & Condensate | CP PUMP forward feedback | U | Run feedback signal | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-324-08-PID-2001 | TM1402 | 35 | 001 | M1 | AL | TM140235U0001M1 | TM140235U001M1_AL |  | Steam & Condensate | CP PUMP alarm | U | Alarm Signal | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-324-08-PID-2001 | TM1402 | 35 | 001 | M1 | RY | TM140235U0001M1 | TM140235U001M1_RY |  | Steam & Condensate | CP PUMP ready to start | U | Ready signal | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-324-08-PID-2001 | TM1402 | 35 | 002 | M1 | STR | TM140235U0002M1 | TM140235U002M1_STR |  | Steam & Condensate | CP PUMP START | U | Start/Stop signal | MCC | DCS | DO | N.O. | profibus |  | DCS Cabinet
P-OKITM08-324-08-PID-2001 | TM1402 | 35 | 002 | M1 | RF | TM140235U0002M1 | TM140235U002M1_RF |  | Steam & Condensate | CP PUMP forward feedback | U | Run feedback signal | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-324-08-PID-2001 | TM1402 | 35 | 002 | M1 | AL | TM140235U0002M1 | TM140235U002M1_AL |  | Steam & Condensate | CP PUMP alarm | U | Alarm Signal | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-324-08-PID-2001 | TM1402 | 35 | 002 | M1 | RY | TM140235U0002M1 | TM140235U002M1_RY |  | Steam & Condensate | CP PUMP ready to start | U | Ready signal | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-324-08-PID-2001 | TM1402 | 35 | 003 | M1 | STR | TM140235U0003M1 | TM140235U003M1_STR |  | Steam & Condensate | CP PUMP START | U | Start/Stop signal | MCC | DCS | DO | N.O. | profibus |  | DCS Cabinet
P-OKITM08-324-08-PID-2001 | TM1402 | 35 | 003 | M1 | RF | TM140235U0003M1 | TM140235U003M1_RF |  | Steam & Condensate | CP PUMP forward feedback | U | Run feedback signal | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-324-08-PID-2001 | TM1402 | 35 | 003 | M1 | AL | TM140235U0003M1 | TM140235U003M1_AL |  | Steam & Condensate | CP PUMP recirculating fan alarm | U | Alarm Signal | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-324-08-PID-2001 | TM1402 | 35 | 003 | M1 | RY | TM140235U0003M1 | TM140235U003M1_RY |  | Steam & Condensate | CP PUMP ready to start | U | Ready signal | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-324-08-PID-2001 | TM1402 | 35 | 004 | M1 | STR | TM140235U0004M1 | TM140235U004M1_STR |  | Steam & Condensate | CP PUMP START | U | Start/Stop signal | MCC | DCS | DO | N.O. | profibus |  | DCS Cabinet
P-OKITM08-324-08-PID-2001 | TM1402 | 35 | 004 | M1 | RF | TM140235U0004M1 | TM140235U004M1_RF |  | Steam & Condensate | CP PUMP forward feedback | U | Run feedback signal | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-324-08-PID-2001 | TM1402 | 35 | 004 | M1 | AL | TM140235U0004M1 | TM140235U004M1_AL |  | Steam & Condensate | CP PUMP recirculating fan alarm | U | Alarm Signal | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-324-08-PID-2001 | TM1402 | 35 | 004 | M1 | RY | TM140235U0004M1 | TM140235U004M1_RY |  | Steam & Condensate | CP PUMP ready to start | U | Ready signal | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-335-08-PID-2001 | TM1402 | 33 | 002 | M1 | STR | TM140233F0002M1 | TM140233F002M1_STR |  | Dust Removal & Mist Removal | SUCTION fan start | F | SUCTION fan start | MCC | DCS | DO | N.O. | profibus |  | DCS Cabinet
P-OKITM08-335-08-PID-2001 | TM1402 | 33 | 002 | M1 | RF | TM140233F0002M1 | TM140233F002M1_RF |  | Dust Removal & Mist Removal | SUCTION fan forward feedback | F | SUCTION fan forward feedback | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-335-08-PID-2001 | TM1402 | 33 | 002 | M1 | AL | TM140233F0002M1 | TM140233F002M1_AL |  | Dust Removal & Mist Removal | SUCTION fan alarm | F | SUCTION fan alarm | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-335-08-PID-2001 | TM1402 | 33 | 002 | M1 | RY | TM140233F0002M1 | TM140233F002M1_RY |  | Dust Removal & Mist Removal | SUCTION fan ready to start | F | SUCTION fan ready to start | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-335-08-PID-2001 | TM1402 | 33 | 002 | M1 | CURR | TM140233F0002M1 | TM140233F002M1_CURR |  | Dust Removal & Mist Removal | SUCTION fan current | F | SUCTION fan current | MCC | DCS | AI | 4-20mA | profibus |  | DCS Cabinet
P-OKITM08-335-08-PID-2001 | TM1402 | 33 | 002 | M1 | SPC | TM140233F0002M1 | TM140233F002M1_SPC |  | Dust Removal & Mist Removal | SUCTION fan speed reference | F | SUCTION fan speed reference | MCC | DCS | AO | 4-20mA | profibus |  | DCS Cabinet
P-OKITM08-335-08-PID-2001 | TM1402 | 33 | 001 | M1 | STR | TM140233U0001M1 | TM140233U001M1_STR |  | Dust Removal & Mist Removal | CP PUMP START | U | Start/Stop signal | MCC | DCS | DO | N.O. | profibus |  | DCS Cabinet
P-OKITM08-335-08-PID-2001 | TM1402 | 33 | 001 | M1 | RF | TM140233U0001M1 | TM140233U001M1_RF |  | Dust Removal & Mist Removal | CP PUMP forward feedback | U | Run feedback signal | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-335-08-PID-2001 | TM1402 | 33 | 001 | M1 | AL | TM140233U0001M1 | TM140233U001M1_AL |  | Dust Removal & Mist Removal | CP PUMP recirculating fan alarm | U | Alarm Signal | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-335-08-PID-2001 | TM1402 | 33 | 001 | M1 | RY | TM140233U0001M1 | TM140233U001M1_RY |  | Dust Removal & Mist Removal | CP PUMP ready to start | U | Ready signal | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-336-08-PID-2001 | TM1402 | 33 | 001 | M1 | STR | TM140233F0001M1 | TM140233F001M1_STR |  | Dust Removal & Mist Removal | SUCTION fan start | F | SUCTION fan start | MCC | DCS | DO | N.O. | profibus |  | DCS Cabinet
P-OKITM08-336-08-PID-2001 | TM1402 | 33 | 001 | M1 | RF | TM140233F0001M1 | TM140233F001M1_RF |  | Dust Removal & Mist Removal | SUCTION fan forward feedback | F | SUCTION fan forward feedback | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-336-08-PID-2001 | TM1402 | 33 | 001 | M1 | AL | TM140233F0001M1 | TM140233F001M1_AL |  | Dust Removal & Mist Removal | SUCTION fan alarm | F | SUCTION fan alarm | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-336-08-PID-2001 | TM1402 | 33 | 001 | M1 | RY | TM140233F0001M1 | TM140233F001M1_RY |  | Dust Removal & Mist Removal | SUCTION fan ready to start | F | SUCTION fan ready to start | MCC | DCS | DI | N.O. | profibus |  | DCS Cabinet
P-OKITM08-336-08-PID-2001 | TM1402 | 33 | 001 | M1 | CURR | TM140233F0001M1 | TM140233F001M1_CURR |  | Dust Removal & Mist Removal | SUCTION fan current | F | SUCTION fan current | MCC | DCS | AI | 4-20mA | profibus |  | DCS Cabinet
P-OKITM08-336-08-PID-2001 | TM1402 | 33 | 001 | M1 | SPC | TM140233F0001M1 | TM140233F001M1_SPC |  | Dust Removal & Mist Removal | SUCTION fan speed reference | F | SUCTION fan speed reference | MCC | DCS | AO | 4-20mA | profibus |  | DCS Cabinet

## IO Summary
I/O LIST COUNT SUMMARY
AREA DESCRIPTION | AREA NO. | AI | AO | DI | DO | Sum | SYSTEM
Wet End | 30 | 4 | 5 | 43 | 18 | 70 | DCS
Dry End | 31 | 10 | 4 | 79 | 65 | 158
Burner & Hood System | 32 | 10 | 0 | 35 | 4 | 49
Dust & Mist Removal | 33 | 13 | 7 | 16 | 3 | 39
Lubrication & Hydraulic | 34 | 16 | 4 | 16 | 16 | 52
Steam & Condensate | 35 | 13 | 11 | 4 | 2 | 30
| DCS (Total) | 66 | 31 | 193 | 108 | 398
SIGNAL EXCHANGE LIST COUNT SUMMARY (PROFIBUS)
AREA DESCRIPTION | AREA NO. | AI | AO | DI | DO | Sum
Wet End | 30 | 0 | 0 | 24 | 14 | 38
Dry End | 31 | 1 | 1 | 9 | 5 | 16
Burner & Hood System | 32 | 4 | 4 | 22 | 24 | 54
Dust & Mist Removal | 33 | 2 | 2 | 9 | 3 | 16
Lubrication & Hydraulic | 34 | 0 | 0 | 14 | 7 | 21
Steam & Condensate | 35 | 0 | 0 | 12 | 4 | 16
ETC. |  | 0 | 0 | 0 | 0 | 0
SAFETY | 31 | 0 | 0 | 28 | 14 | 42
| DCS (Total) | 7 | 7 | 118 | 71 | 203
Note on C10: [Komentarz podzielony na wątki] Używana wersja programu Excel umożliwia odczytanie tego komentarza podzielonego na wątki, jednak wszelkie wprowadzone w nim zmiany zostaną usunięte po otwarciu pliku w nowszej wersji programu Excel. Dowiedz się więcej: https://go.microsoft.com/fwlink/?linkid=870924 Komentarz: The total quantity in this row is belong to the DCS I/O

## Definitions
P&ID No. | The P&ID drawing number where the equipment is located. |  | Appendix 5 – Instrument Code
Area | The Area where the equipment is located |  | CODE | DESCRIPTION
Loop No. | Loop Number |  | HV | OnOff/Ctr. Valve/Manual Control from DCS
Tag No. | Tag Name according to APP guideline |  | SV | Solenoid Valve
System Tag No. | Tag name to be appeared in DCS |  | GS | Limit Switch Post Gap Refiner
Service Description | Process/service description |  | GI | Limit Switch Gap Headbox
Signal Tag | Signal Tagname |  | GT | Limit Transmitter
Instrument Type | Type of instrument |  | GE | Limit Switch Element
Location | Location of the instrument |  | SC | Speed Control
System | in DCS, PLC or local |  | AI | Freeness Analyzer Indication
IO Type | Type of input or output |  | AC | Ph Analyzer
Signal - Type | Signal type |  | AT | Analyzer Transmitter
Signal - Power | Power for the signal |  | AE | Analyzer Element
Signal - Wire | wiring configuration |  | EC | Lamp, Alarm, Sensor
IO Loc. | Input and Output location |  | JC | Power Refiner
PV LO | Range Low |  | JT | Power Refiner Transmitter
PV HI | Range High |  | JI | Power Refiner Indication
Eng. Unit | Engineering Unit |  | LC | Level Control
Alarm | LLL- Low Low Low, HHH- High High High etc |  | LS | Level Switch
State "0" | For Valves, If signal is zero, what willl be the valve opening. |  | LI | Level Indication
State "1" | For Valves, If signal is one, what willl be the valve opening. |  | LT | Level Transmitter
CV fail Action | For Valves, If air fails, what willl be the valve status. |  | LV | Level Valve
CV Control Action | For Valves, Direction of the control. |  | FC | Flow Control
PV CHAR | Process value characteristics |  | FS | Flow Safety
Rev | Revision |  | FI | Flow Indication
Supply By | Supplier name |  | FT | Flow Transmitter
Remarks |  |  | FV | Flow Valve
|  |  | FE | Flow Element
|  |  | PC | Pressure Control
|  |  | PDI | Pressure Differential
|  |  | PS | Pressure Switch
|  |  | PI | Pressure Indication
|  |  | PT | Pressure Transmitter
|  |  | PV | Pressure valve
|  |  | TC | Temp. Control
|  |  | TI | Temp. Indication
|  |  | TT | Temp. Transmitter
|  |  | TV | Temp. Valve
|  |  | TE | Temp. Element
|  |  | NC | Consistency Control
|  |  | NI | Consistency Indication
|  |  | NT | Consistency Transmitter
|  |  | NV | Consistency Valve
|  |  | KS | Time Switch
|  |  | KV | Valve Junk Trap
|  |  | WIC | Weight Indication Control
|  |  | M | Motor
|  |  | MT | Moisture Transmitter
|  |  | WT | Weight Transmitter
|  |  | UE | Multi-function device
|  |  | GSO | Limit Switch Gap Headbox Open
|  |  | GSC | Limit Switch Gap Headbox Close
|  |  | HS | Push button
|  |  | XL | Lamp
|  |  | ZI | Display
|  |  | WI | Weight Indication
|  |  | XA | Horn
|  |  | ESV | Safety Solenoid Valve
|  |  | GSE | Safety Limit Switch Element
|  |  | CR | Control relay
|  |  | CX | Control relay contact
|  |  | HSS | Emergency mushroom button
|  | Common (Basic) Motors | RY | Ready signal
|  |  | RF | Run feedback signal
|  |  | STR | Start/Stop signal
|  |  | CURR | Current signal (A)
|  |  | POW | Power signal (kWh)
|  | Frequency Drives | SI | Speed signal (rpm)
|  |  | SPC | Speed setpoint signal (rpm)
|  | Forward/Reverse Motors | STRF | Start forward signal
|  |  | STRR | Start reverse signal
|  |  | FWDR | Run feedback forward signal
|  |  | REVR | Run feedback reverse signal
|  | Motorized Valves | OPN | Open valve
|  |  | CLS | Close valve
|  |  | ZSO | Open limit switch signal
|  |  | ZSC | Close limit switch signal
|  |  | WSO | Open torque switch signal
|  |  | WSC | Close torque switch signal
|  |  | WSH | Torque switch high signal
|  |  | 0 | Cranes, Hoists, Transf. Sys., Grinding Machine, Tools
|  |  | 1 | Air compressor station
|  |  | 2 | Laboratory Equipment
|  |  | 3 | Electrical
|  |  | 10 | Buffer Area
|  |  | 11 | NBKP Line
|  |  | 12 | LBKP Line
|  |  | 15 | Chemical Preparation (Talc, Caustic, Starch)
|  |  | 16 | Chemical (WSD, DSA, Coating)
|  |  | 17 | Broke System
|  |  | 20 | Approach System
|  |  | 21 | White Water & Fiber Recovery System
|  |  | 22 | Fresh Water System
|  |  | 23 | Vacuum System
|  |  | 30 | Wet End
|  |  | 31 | Dry End
|  |  | 32 | Burner & Hood System
|  |  | 33 | Dust Removal & Mist Removal
|  |  | 34 | Lubrication, Hydraulic system
|  |  | 35 | Steam & Condensate
|  |  | 40 | Un Wind
|  |  | 41 | Calender
|  |  | 42 | Winder
|  |  | 49 | DCS, PLC, QCS
|  |  | 50 | Conveyor
|  |  | 51 | Wrapping